## Slide 1
ELECTRICAL TRADES
Maximum Demand
Single Phase Domestic Installation

## Slide 2: Introduction
Calculate the Maximum Demand of a single phase domestic installation using AS/NZS 3000 : 2007
- Determine the cable size of the consumer main from the Maximum Demand calculated.
- Cable size with reference to WA Requirements and AS/NZS 3008.1.1

## Slide 3
Items to be installed:
22 x lighting points,
4 x single socket outlets
15 x double socket outlets
1 x 15 amp socket outlet,
1 x 4.8 kw Hot Water Heater (Storage)
1 x 3.8 kW Wall Oven.
1 x 4.8 kW Hot Plates
1 x 1.2 kW Pool Pump
4 x 500 W Pool Lighting
2 x 250 W Security Lighting
1 x 2.4 kW Air Conditioner @ 12 Amps
Type of connection : Cable is Two Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.
Single Phase Residential
Type of installation : Single domestic only

## Slide 4: AS/NZS 3000 : 2007, Appendix C, Table C1, Column 2, Single Domestic
  Determine Electrical requirements with
  regards to Load Groups - Column 1

## Slide 5: Load group A Lighting A (i) General lighting
ie 1 to 20 points = 3 Amps
ie 21 to 40 points = 2 Amps
Total Current = 5 Amps
22 Lighting Points

## Slide 6
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A

## Slide 7: Load group A ( ii ) Lighting
Outdoor lighting, Exceeding 1000 W, Derating 75%
Rating x Derating factor (0.75)
Voltage
Total Current = 8.15 Amps
4 x 500 W Pool Lighting = 2000 W
2 x 250W Security Lighting = 500 W
2500 W x 0.75
230 V

## Slide 8
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A

## Slide 9: Socket Outlets Load group B( i ) Not exceeding 10 Amps
Footnote h Double outlets equal 2 points
4 Single Socket outlets = 4 pts
15 Double Socket Outlets = 30 pts
ie 34 pts
1 to 20 pts = 10 Amps
21 to 40 pts = 5 Amps
Total Current = 15 Amps

## Slide 10
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A = 34 Points | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15A

## Slide 11: Socket Outlets Load group B( ii ) one or more 15 Amps
10 amps irrespective of the number of points
Total Current = 10 Amps

## Slide 12
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A = 34 Points | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15A
4 | Socket Outlet 15 A | B (ii) |  | 10 Amps | 10 A

## Slide 13
Load Group C
Ranges, Cooking Appliances and Laundry equipment.
3.8 kW Wall Oven
4.8 kW Hot Plates
3800 W + 4800 W x 0.5 = 18.7 Amps
230 V
Total Current = 18.7 Amps
50% of connected load

## Slide 14
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A = 34 Points | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15A
4 | Socket Outlet 15 A | B (ii) |  | 10 Amps | 10 A
5 | 3.8 kW Oven & 4.8 kW Hot Plates | C | 50 % | 3800 W+ 4800 W x 0.5 230 V | 18.7 A

## Slide 15
Load Group D
Fixed Space Heating or Air Conditioning
2.4 kW Air Conditioner @ 12 Amps
12 A x 0.75 = 9 Amps
75% of connected load
Total Current = 9 Amps

## Slide 16
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A = 34 Points | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15A
4 | Socket Outlet 15 A | B (ii) |  | 10 Amps | 10 A
5 | 3.8 kW Oven & 4.8 kW Hot Plates | C | 50 % | 3800W + 4800W x 0.5 230 V | 18.7 A
6 | 2.4 kW A/C | D | 75 % | 12 A x 0.75 = 9 A | 9 A

## Slide 17
4800 W = 20.86 Amps
230 V
Total Current = 20.86 Amps
Load Group F Storage Hot Water System
4.8 kW Hot Water System
100% of connected load

## Slide 18
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A = 34 Points | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15A
4 | Socket Outlet 15 A | B (ii) |  | 10 Amps | 10 A
5 | 3.8kW Oven & 4.8 kW Hot Plates | C | 50 % | 3800 W + 4800 W x 0.5 230 V | 18.7 A
6 | 2.4 kW A/C | D | 75 % | 12 A x 0.75 = 9 A | 9 A
7 | 4.8 kW HWS Storage | F | 100% | 4800 W = 20.86 A 230 V | 20.86 A

## Slide 19: Pool Pump 1.2 kW
At  8 Amps per kW (1000 W / 230V x 0.7 x 0.8 = 7.76A) = 1.2 x 8 = 9.6 Amps
Therefore for the purpose of maximum demand it will be connected to the supply via a 10 or 15 Amp Socket Outlet, and will therefore not change the loading of Load Group B ( i ) or B ( ii )

## Slide 20
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A 34 +1(Motor)=35 PTS | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15 A
4 | Socket Outlet 15 A | B (ii) |  | 10 Amps | 10 A
5 | 3.8kW Oven & 4.8 kW Hot Plates | C | 50 % | 3800 W + 4800W x 0.5 230 V | 18.7 A
6 | 2.4 kW A/C | D | 75 % | 12 A x 0.75 = 9 A | 9 A
7 | 4.8 kW HWS Storage | F | 100% | 4800 W = 20.86 A 230 V | 20.86 A

## Slide 21
Item |  | Load Group | Factor % | Calculated Demand | Maximum Current
1 | Lighting 22 points | A (i) |  | 1 to 20 = 3 Amps 21 to 40 = 2 Amps | 5 A
2 | Outdoor Lighting | A (ii) | 75% | (4 x 500W) + (2 x 250W) x 0.75 230 V | 8.15 A
3 | Socket Outlets 10A 34 +1(Motor)=35 PTS | B (i) |  | 1 to 20 = 10 Amps 21 to 40 = 5 Amps | 15 A
4 | Socket Outlet 15 A | B (ii) |  | 10 Amps | 10 A
5 | 3.8kW Oven 4.8 kW HP | C | 50 % | 3800 W + 4800W x 0.5 230 V | 18.7 A
6 | 2.4 kW AC | D | 75 % | 12 A x 0.75 = 8 A | 9 A
7 | 4.8 kW HWS Storage | F | 100% | 4800 W = 20.86 A 230 V | 20.86 A
MAXIMUM DEMAND |  |  |  |  | 86.71 A

## Slide 22: WA Electrical Requirements, Section 12
12.2 Consumer Mains
(a) Single domestic installation where the minimum current carrying capacity shall be:
Special Requirements for Installations in WA
(i) Single phase 63 A
(ii) Multiphase 32 A per phase

## Slide 23: WA Electrical Requirements, Section 5 Underground Supply
5.3 Types of Cables and Enclosures
Cables shall be installed in a heavy duty
non metallic enclosure.
Enclosures shall comply with AS 2053 and be installed a minimum 500 mm below finished ground level.

## Slide 24: AS 3008.1.1- 2009
Table 3 (4 )
Installation methods for cables enclosed in Underground Pipes and Ducts.
Item 3
One Two Core Cable
Table 10 & 11 (Pg 51) - Columns 25, 26 & 27
Table 12 (Pg 51) - Columns 14 & 15

## Slide 25: AS 3008.1.1- 2009
Cable is Two Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.
Table 10 - Current carrying Capacity of Two Core, Sheathed cables with or without earth core, armoured or un armoured, including neutral screened cables.
We therefore use Column 25

## Slide 26: Installation of Consumer Mains
Maximum Demand worked out for this installation is 87 Amps.
Therefore we use :
Cable 25 mm2 Copper ( 112 Amps ) Two Core TPS installed in Heavy Duty Conduit, 500 mm, below Finished Ground Level.

## Slide 27
End of Show This has been a G I Luff Production for the use of the Electrical Trades.