## Slide 1
ELECTRICAL TRADES
Maximum Demand
Three Phase Domestic Installation

## Slide 2: Introduction
Calculate the Maximum Demand of a single phase domestic installation using AS/NZS 3000:2007
Determine the cable size of the consumer main from the Maximum Demand with reference to WA Requirements and AS/NZS 3008.1.1

## Slide 3
Items to be installed:
32 X lighting points,
18 X single socket outlets
6 X double socket outlets
2 X 15 amp socket outlet
1 X 5.4 kW, 3 Phase Instantaneous HWS
1 X 6 kW Wall Oven.
1 X 4.8 kW Hot Plates
1 X 1.2 kW Pool Pump
1 X 5 kW Tennis Court Lighting
1 X 3 kW, 3 Phase Reticulation Pump
1 X 3.4 kW, 3 Phase Air conditioner @ 6 A/ Phase
Type of connection: Three phase underground supply
Three Phase Residential
Type of installation: Cable is Three Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.

## Slide 4: AS/NZS 3000:2007, Appendix C, Table C1, Column 2 Single Domestic
  Determine electrical requirements with
  regards to Load Groups - Column 1

## Slide 5: Load group A Lighting
A i General lighting
1 to 20 points = 3 Amps
21 to 40 points = 2 Amps
Total current = 5 Amps
ie 32 Lighting Points

## Slide 6
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5 A
Socket outlets 41 points | B(ii) | 15 = 10.4 20 = 12.6 6 = 6.5 1000 + (14 x 100) = 10.4 etc | 10.4 | 12.6 | 6.5
3 x 3Ф 15A Socket outlets | B(iii) | Full rating for first then 75% 15 + (30 x .75) = 37.5 | 37.5 | 37.5 | 37.5
3kW Hot plate | C | Full current for highest + 75% | 13 |  | 
4.8kW oven | C | Full current for highest + 75% |  |  | 20.9
3Ф Aircon 4kW @ 0.9 PF | C | Full current for highest + 75% 4000 W x = √ 3 ( ie 1.73) x 400 V x 0.9 = 4000 W = 6.4A / Ø 622.8 | 6.4 | 6.4 | 6.4
Total |  |  |  |  | 

## Slide 7: Load group A Lighting
5000 W x 0.75 =
230 V
16.3 Amps
Rating x De-rating factor (0.75)
Voltage
A ( ii ) Outdoor lighting, exceeding 1000 W, derating 75%

## Slide 8
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5 A
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 230 V |  | 16.3 A | 
Total |  |  |  |  | 

## Slide 9: Socket Outlets Load group B( i ) Not exceeding 10 Amps
Footnote h Double outlets equal 2 points
18 Single Socket outlets = 18 pts
6 x 2 Double Socket Outlets = 12 pts
ie 30 pts
Ie 15 outlets x 2
From table
1 to 20 pts = 10 Amps x 2
= 20 Amps Total

## Slide 10
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 230 V |  | 16.3 | 
Socket outlets 30 + 1 points (1 for 1.2kW Pump) | B(i) | 15 = 10A 15 = 10A |  | 10 | 10
3 x 3Ф 15A Socket outlets | B(iii) | Full rating for first then 75% 15 + (30 x .75) = 37.5 |  |  | 
3kW Hot plate | C | Full current for highest + 75% |  |  | 
4.8kW oven | C | Full current for highest + 75% |  |  | 
3Ф Aircon 4kW @ 0.9 PF | C | Full current for highest + 75% 4000 W x = √ 3 ( ie 1.73) x 400 V x 0.9 = 4000 W = 6.4A / Ø 622.8 |  |  | 
Total |  |  |  |  | 

## Slide 11: Socket Outlets Load group B( ii ) one or more 15 Amps
10 amps irrespective of the number of points
ie 10 Amps

## Slide 12
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 230 V |  | 16.3 | 
Socket outlets 31 points | B(i) | 17 = 10A 17 = 10A |  | 10 | 10
Socket Outlet 15 A | B (ii) | 1-20 points = 10 Amps |  |  | 10
3kW Hot plate | C | Full current for highest + 75% |  |  | 
4.8kW oven | C | Full current for highest + 75% |  |  | 
3Ф Aircon 4kW @ 0.9 PF | C | Full current for highest + 75% 4000 W x = √ 3 ( ie 1.73) x 400 V x 0.9 = 4000 W = 6.4A / Ø 622.8 |  |  | 
Total |  |  |  |  | 

## Slide 13
Load Group C
Ranges, Cooking Appliances and Laundry equipment.
at 50% of connected load.
6000 W x 0.5 = 13 Amps
230 V
6 kW Wall Oven
4.8 kW Hot Plates
4800 W x 0.5 = 10.43 Amps
230 V = 10.4Amps

## Slide 14
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 230 V |  | 16.3 | 
Socket outlets 31 points | B(i) | 17 = 10A 17 = 10A |  | 10 | 10
Socket Outlet 15 A | B (ii) | 1-20 points = 10 Amps |  |  | 10
6kW Oven | C | 6000 W x 50 % = 13A 230 V | 13 |  | 
4.8 kW Hot Plate | C | 4800 W x 50 % = 11A 230 V | 10.4 |  | 
3Ф Aircon 4kW @ 0.9 PF | C | Full current for highest + 75% 4000 W x = √ 3 ( ie 1.73) x 400 V x 0.9 = 4000 W = 6.4A / Ø 622.8 |  |  | 
Total |  |  |  |  | 

## Slide 15: Load Group D Fixed Space Heating or Air Conditioning at 75% of connected load
3.4 kW 3 Ф Air conditioner @ 6 A/ Ф
6 Amps x 0.75
4.5 Amps / Ф

## Slide 16
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 230 V |  | 16.3 | 
Socket outlets 31 points | B(i) | 17 = 10A 17 = 10A |  | 10 | 10
Socket Outlet 15 A | B (ii) | 1-20 points = 10 Amps |  |  | 10
6kW Oven | C | 6000 W x 50 % = 13A 230 V | 13 |  | 
4.8 kW Hot Plate | C | 4800 W x 50 % =11A 230 V | 10.4 |  | 
3.4 kW 3 Ф AC @ 6 A/Ф | D | 6 A x 0.75 = 4.5 Ф | 4.5 | 4.5 | 4.5
Total |  |  |  |  | 

## Slide 17
5400 W x .333 = 2.59Amps / Ф
√ 3 ( ie 1.73) x 400 V
ie 2.6 Amps / Ф
Load Group E
Instantaneous Hot Water System at 33.3% of connected load.
5.4 kW Hot Water System

## Slide 18
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  | 5 | 
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 16.3A 230 V | 16.3 |  | 
Socket outlets 31 points | B(i) | 17 = 10A 17 = 10A |  | 10 | 10
Socket Outlet 15 A | B (ii) | 1-20 points = 10 Amps |  |  | 10
6kW Oven | C | 6000 W x 50 % = 13A 230 V |  | 13 | 
4.8 kW Hot Plate | C | 4800 W x 50 % = 11A 230 V | 10.4 |  | 
3.4 kW 3 Ф AC @ 6 A/Ф | D | 6 A x 0.75 = 4.5A | 4.5 | 4.5 | 4.5
5.4kW 3 Ф HWS | E | 5400 W x .333 = 2.6A √3 x 400 V | 2.6 | 2.6 | 2.6
Total |  |  |  |  | 

## Slide 19: Pool Pump 1.2 kW
At 8 Amps per kW (1000 W / 230V x 0.70 x 0.8 = 7.68A) = 1.2 x 8 = 9.6 Amps
Therefore for the purpose of maximum demand it will be connected to the supply via a 10 or 15 Amp Socket Outlet, and will therefore not change the loading of Load Group B ( i ) or B ( ii )

## Slide 20
At (1000 W / 400V x 1.73 x 0.9 x 0.8) = 2 Amps per kW
= 2A x 3 = 6 Amps / Ф
Load Group L 100% for highest rated motor plus 50 % for the remainder.
3 kW 3 Phase Reticulation Pump

## Slide 21
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 1 to 20 = 3 Amps 21 to 40 = 2 Amps |  |  | 5
Outdoor Lighting | A (ii) | 5000 W x 0.75 = 16.3A 230 V |  | 16.3 | 
Socket outlets 31 points | B(i) | 17 = 10A 17 = 10A |  | 10 | 10
Socket Outlet 15 A | B (ii) | 1-20 points = 10 Amps |  |  | 10
6kW Oven | C | 6000 W x 50 % = 13A 230 V | 13 |  | 
4.8 kW Hot Plate | C | 4800 W x 50 % = 11A 230 V | 10.4 |  | 
3.4 kW 3 Ф AC @ 6 A/Ф | D | 6 A x 0.75 = 4.5A | 4.5 | 4.5 | 4.5
5.4kW 3 Ф HWS | E | 5400 W x .333 = 2.6A √3 x 400 V | 2.6 | 2.6 | 2.6
Reticulation Pump 3 kW, 3 Ф | L | 2 Amps per kW = 2 x 3kW = 6A/Ф | 6 | 6 | 6
Total |  |  | 36.5 | 39.6 | 38.1

## Slide 22: WA Electrical Requirements
Section 12
Special Requirements for Installations in WA
(a) Single domestic installation where the minimum current carrying capacity shall be:
(i) Single phase 63A per phase
(ii) Multiphase 32 A per phase
12.2 Consumer Mains

## Slide 23: WA Electrical Requirements
Section 5
Underground Supply
5.3 Types of Cables and Enclosures
Cables shall be installed in a heavy duty non metallic enclosure.
Enclosures shall comply with AS 2053 and be installed a minimum 500 mm below finished ground level.

## Slide 24: AS 3008.1.1- 2009
Table 3 (4 )
Installation Methods for Cables Enclosed in Underground Pipes and Ducts
Item 4 One Three Core Cable
Table 13 & 14 - Columns 25 to 27
Table 15 - Columns 14 & 15

## Slide 25: AS 3008.1.1- 2009
Cable is Three Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.
Table 13 - Current carrying Capacity of Three Core, Sheathed cables with or without earth core, armoured or un armoured, including neutral screened cables.
Column 25 Cu (Copper Cables)
Maximum Demand is 39.6 Amps
Closest cable is 6 mm2 at 42 Amps.

## Slide 26: Installation of Consumer Mains
ie Maximum Demand = 39.6 Amps
Cable 6 mm2 ( 42 Amps ) Four Core TPS
installed in Heavy Duty Conduit 500 mm below
Finished Ground Level.

## Slide 27
End of Show This has been a G I Luff Production for the use of the Electrical Trades.