## Slide 1
ELECTRICAL TRADES
Maximum Demand
Non Domestic Installation

## Slide 2: Introduction
Calculate the Maximum Demand of a three phase non domestic installation using AS/NZS 3000
Determine the cable size of the consumer main from the Maximum Demand with reference to WA Requirements and AS/NZS 3008.1.1

## Slide 3: Non Domestic Installation
Calculate the Maximum Demand for the following installation.
Cable is Four Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.

## Slide 4
Items to be installed:
  20 x 500 W HP sodium vapour lamps @ 3.25 A/unit.
  10 x Double 36 W fluorescent units(use 400mA per unit)
  x 150 W LP sodium vapour security lamps @ 2.8A/unit over fuel
  dispensing area.
  8 x 10A single outlets in the factory workshop.
  15 x 10A double outlets in the factory workshop.
  10 x 10A double outlets in factory office (airconditioned)
  6 x 15 amp outlets in factory workshop.
  6 x 32 amp, 3 phase outlets.
  6 x 15 amp, 3 phase outlets.
  1 x 10 kW, 3 phase air conditioner @18 amp/phase for factory office.
  3 x 5.4 kW, 3 phase instantaneous HWS
  1 x 4.8 kW 1 phase stove.
  1 x 10 kW, 3 phase hydraulic pump motor.
  2 x 5 kW, 3 phase lathe motors.
  2 x 1.5 kW, 1 phase drill motors.
  2 x 1.25 kW, 1 phase fuel pumps.
  3 x 10 kW at 21 A/Phase 2 phase welders.
Non Domestic Factory Units

## Slide 5: AS/NZS 3000:2007, Appendix C, Table C2, Page 359
Columns 2 deals with Residential institutions, hotels, hospitals , motels etc
Columns 3 deals with Factories, shops, stores , offices schools, etc

## Slide 6: AS/NZS 3000:2007 Appendix C, Table C2, Page No 359
A Factory Unit
  Determine Electrical requirements with regards to Load Groups - Column 3
  Three Phase Motors
At (1000 W / 400V x 1.73 x 0.9 x 0.8) = 2 Amps per kW = 2A x 3 = 6 Amps / Ф

## Slide 7: Load group A Lighting
Lighting other than load Group F
and
Double 36 W Fluro = 400 mA x 10 = 4 Amps
Total Current is 7 x 3.25A = 22.75A
7 x 3.25A = 22.75A
6 x 3.25A = 19.5A + 4 A = 23.5A
Full connected load
20 x 500 W HP Sodium Vapour Lamps @ 3.25 A/Unit
10 Double x 36 W Fluorescent Units

## Slide 8
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 30 points | A (i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 =23.5A | 22.8 | 22.8 | 23.5
Total |  |  |  |  | 

## Slide 9: Socket Outlets Load group B( i ) Not exceeding 10 Amps NO Air Conditioning
Footnote h states - Double outlets equal 2 points.
8 x single outlets in the factory workshop
15 x double outlets in the factory workshop
Using 1000 W for the first, plus 750W for each additional.
1000 W + (12 x 750 W) = 43.47 A
230 V
+ (15 x 2 ) = 38 outlets
ie split to 2 x 13 & 1 x 12 = 38 outlets
1000 W + (11 x 750 W) = 40.21 A
230 V
1000 W + (12 x 750 W) = 43.47 A
230 V

## Slide 10
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A (i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps | B (i) | 13 = 43.47A x 2 & 12 = 40.21A | 40.2 | 43.5 | 43.5
Total |  |  |  |  | 

## Slide 11: Socket Outlets Load group (Bii). Socket outlets not exceeding 10A in buildings. With permanently installed heating & cooling.
10 x double outlets for air conditioning in the factory office i.e. 20 GPOs
1000W for first socket outlet, plus 100W for each additional outlet.
ie split to 2 x 7 & 1 x 6 = 20 outlets
1000 W + (6 x 100 W) = 6.95 A
230 V
1000 W + (5 x 100 W) = 6.52 A
230 V
1000 W + (6 x 100 W) = 6.95 A
230 V

## Slide 12
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 40.2 | 43.5 | 43.5
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
Total |  |  |  |  | 

## Slide 13: Socket Outlets Load group B( iii ) one or more 15 Amps
Full current of the highest rated socket plus 75% of full current rating of the remainder
6 x 15 Amp Socket Outlets
Full load + 75% of rest
15A + (15A x0.75) = 26.25A
15A + (15A x0.75) = 26.25A
15A + (15A x0.75) = 26.25A
Single Phase

## Slide 14
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 40.2 | 43.5 | 43.5
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
1Ф, 15 A Outlets | B(iii) | 15A + (15A x0.75) = 26.25A x 3 | 26.3 | 26.3 | 26.3
Total |  |  |  |  | 

## Slide 15: Socket Outlets Load group B( iii ) one or more 15 Amps
Full current of the highest rated socket plus 75% of full current rating of the remainder.
6 x 32 A being 3 Phase Outlets
6 x 15 A being 3 Phase Outlets
1 at 100% = 32 Amps
(5 x 32 A) x 0.75 = 120 Amps
(6 x 15 A) x 0.75 = 67.5 Amps
Total Current – 219.5 Amps (per Phase)
Three Phase

## Slide 16
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 40.2 | 43.5 | 43.5
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
1Ф, 15 A Outlets | B(iii) | 15A + (15A x0.75) = 26.25A x 3 | 26.3 | 26.3 | 26.3
3Ф Outlets | B(iii) | 1 at 100% = 32 Amps (5 x 32 A) x 0.75 = 120 Amps (6 x 15 A) x 0.75 = 67.5 Amps | 219.5 | 219.5 | 219.5
Total |  |  |  |  | 

## Slide 17
Load Group C
Appliances for cooking, heating and cooling and Laundry equipment.
  1 x 10 kW, 3 Ф Air conditioner @ 18 amp/phase for factory office
  3 x 5.4 kW 3 Ф Instantaneous HWS
  1 x 4.8 kW stove
4800 W x 0.75 = 15.65 A
230 V
1 x 10 kW 3Ф Air conditioner = 18 AmpsФ
3 x 5.4 kW 3Ф Inst HWS x 0.75 = 17.53 AmpsФ
1 x 4.8 kW 1Ф stove x 0.75 = 15.65 Amps
5400 W x 0.75 x 3 = 17.53A
√ 3 x 400 V
100% for the highest 75% for the remainder

## Slide 18
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 43.5 | 43.5 | 40.2
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
1Ф, 15 A Outlets | B(iii) | 15A + (15A x0.75) = 26.25A x 3 | 26.3 | 26.3 | 26.3
3Ф Outlets | B(iii) | 1 at 100% = 32 Amps (5 x 32 A) x 0.75 = 120 Amps (6 x 15 A) x 0.75 = 67.5 Amps | 219.5 | 219.5 | 219.5
Cooking | C | 4800 W x 0.75 = 15.65A 230 V | 15.7 |  | 
Air Conditioner | C | 10 KW, 3 Ph A/C18 A / Phase | 18 | 18 | 18
Instantaneous HWS, 3Ф | C | 5400 W x 3 = 23.4A x 0.75 1.73 x 400 V | 17.5 | 17.5 | 17.5
Total |  |  |  |  | 

## Slide 19: Load Group D Motors other than Lifts & Fuel Dispensing
  1 x 10 kW , 3 phase hydraulic pump motor
  2 x 5 kW , 3 phase lathe motors
  2 x 1.5 kW , 1 phase drill motors
Full load of the highest rated motor.
Plus 75% of full load of the second
Plus 50% of full load of the remainder
1 x 10 kW x 2 A / kW = 20 Amps
1 x 1.5 kW x 8 A / kW x 0.5 = 6.0 Amps
1 x 1.5 kW x 8 A / kW x 0.5 = 6.0 Amps
1 x 5 kW x 2 A / kW x 0.75 = 7.5 Amps
1 x 5 kW x 2 A / kW x 0.5 = 5.0 Amps

## Slide 20
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 40.2 | 43.5 | 43.5
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
1Ф, 15 A Outlets | B(iii) | 15A + (15A x0.75) = 26.25A x 3 | 26.3 | 26.3 | 26.3
3Ф Outlets | B(iii) | 1 at 100% = 32 Amps (5 x 32 A) x 0.75 = 120 Amps (6 x 15 A) x 0.75 = 67.5 Amps | 219.5 | 219.5 | 219.5
Cooking | C | 4800 W x 0.75 = 15.65A 230 V | 15.7 |  | 
Air Conditioner | C | 10 KW, 3 Ph A/C18 A / Phase | 18 | 18 | 18
Instant HWS, 3Ф | C | 5400 W x 3 = 23.4A x 0.75 1.73 x 400 V | 17.5 | 17.5 | 17.5
SUB TOTAL |  |  | 367.7 | 356 | 355.3
CONTINUED ON NEXT PAGE |  |  |  |  | 

## Slide 21
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
10 KW 3ФHydraulic Pump | D | 10 kW x 2 A/ kW = 20A/Ф | 20 | 20 | 20
1 x 5 KW 3ФLathe Motors | D | 5 kW x 2 A/kW x 0.75 = 7.5A/Ф | 7.5 | 7.5 | 7.5
1x 5 KW 3ФLathe Motors | D | 5 kW x 2 A/kW x 0.5 = 5A/Ф | 5 | 5 | 5
1 x 1.5 KW Drill Motors | D | 1.5 kW x 8 A/kW x 0.5 = 6A | 6 |  | 
1 x 1.5 KW Drill Motors | D | 1.5 kW x 8 A/kW x 0.5 = 6A |  |  | 6
Total |  |  |  |  | 

## Slide 22: Load Group F Fuel Dispensing
  2 x 1.25 kW, 1 Phase Fuel Pumps
Full load of the highest rated motor.
Plus 50% of full load of the second
Plus 25% of full load of the remainder
1.25kW x 8 A/kW = 10A
1.25kW x 8 A/kW x 0.5 = 5A
  5x 150 W LP sodium vapour security lamps @ 2.8A/unit
  5 x 2.8 A = 14 A
Lighting 100% connected Load

## Slide 23
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 40.2 | 43.5 | 43.5
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
1Ф, 15 A Outlets | B(iii) | 15A + (15A x0.75) = 26.25A x 3 | 26.3 | 26.3 | 26.3
3Ф Outlets | B(iii) | 1 at 100% = 32 Amps (5 x 32 A) x 0.75 = 120 Amps (6 x 15 A) x 0.75 = 67.5 Amps | 219.5 | 219.5 | 219.5
Cooking | C | 4800 W x 0.75 = 15.65A 230 V | 15.7 |  | 
Air Conditioner | C | 10 KW, 3 Ph A/C18 A / Phase | 18 | 18 | 18
Instant HWS, 3Ф | C | 5400 W x 3 = 23.4A x 0.75 1.73 x 400 V | 17.5 | 17.5 | 17.5
SUB TOTAL |  |  | 367.7 | 356 | 355.3
CONTINUED ON NEXT PAGE |  |  |  |  | 

## Slide 24
Load | Load Group | Calculations | Red Phase | White Phase | Blue Phase
10 KW 3ФHydraulic Pump | D | 10 kW x 2 A/ kW = 20A/Ф | 20 | 20 | 20
1 x 5 KW 3ФLathe Motors | D | 5 kW x 2 A/kW x 0.75 = 7.5A/Ф | 7.5 | 7.5 | 7.5
1x 5 KW 3ФLathe Motors | D | 5 kW x 2 A/kW x 0.5 = 5A/Ф | 5 | 5 | 5
1 x 1.5 KW Drill Motors | D | 1.5 kW x 8 A/kW x 0.5 = 6A | 6 |  | 
1 x 1.5 KW Drill Motors | D | 1.5 kW x 8 A/kW x 0.5 = 6A |  |  | 6
1 x 1.25 kW Fuel Pumps | F | 1.25kW x 8 A/kW |  | 10 | 
1 x 1.25 kW Fuel Pumps | F | 1.25kW x 8 A/kW x 0.5 |  | 5 | 
5 x 150 W Sodium Vapour | F | 5 x 2.8 A / Unit |  |  | 14
Total |  |  |  |  | 

## Slide 25: Load Group H Welding Machines
  3 x 10 kW at 21 A/Phase 2 Phase Welders
100% for the first 2 machines
85 % for the next largest machine
70 % for the next largest
60 % for all others machines
21A x 2 = 2 x 21 and 21 Amps per phase
21A x 0.85 = 17.85 Amps per phase

## Slide 26
Load | Load Group | Calculations | Red Phase | White Phase | Blue phase
Lighting 32 points | A(i) | 7 = 22.75A x 2 & 6 = 19.5A + 4 = 23.5A | 22.8 | 22.8 | 23.5
Outlets 10 Amps (Non Aircon) | B(i) | 13 = 43.47A x 2 & 12 = 40.21A | 43.5 | 43.5 | 40.2
Outlets 10 Amps (With Aircon) | B(ii) | 7 = 6.95A x 2 & 6 = 6.52A | 7.0 | 7.0 | 6.5
1Ф, 15 A Outlets | B(iii) | 15A + (15A x0.75) = 26.25A x 3 | 26.3 | 26.3 | 26.3
3Ф Outlets | B(iii) | 1 at 100% = 32 Amps (5 x 32 A) x 0.75 = 120 Amps (6 x 15 A) x 0.75 = 67.5 Amps | 219.5 | 219.5 | 219.5
Cooking | C | 4800 W x 0.75 = 15.65A 230 V | 15.7 |  | 
Air Conditioner | C | 10 KW, 3 Ph A/C18 A / Phase | 18 | 18 | 18
Instant HWS, 3Ф | C | 5400 W x 3 = 23.4A x 0.75 1.73 x 400 V | 17.5 | 17.5 | 17.5
SUB TOTAL |  |  | 367.7 | 356 | 355.3
CONTINUED ON NEXT PAGE |  |  |  |  | 

## Slide 27
Load | Load Group | Calculations | Red Phase | White Phase | Blue Phase
10 KW 3ФHydraulic Pump | D | 10 kW x 2 A/ kW = 20A/Ф | 20 | 20 | 20
1 x 5 KW 3ФLathe Motors | D | 5 kW x 2 A/kW x 0.75 = 7.5A/Ф | 7.5 | 7.5 | 7.5
1x 5 KW 3ФLathe Motors | D | 5 kW x 2 A/kW x 0.5 = 5A/Ф | 5 | 5 | 5
1 x 1.5 KW Drill Motors | D | 1.5 kW x 8 A/kW x 0.5 = 6A | 6 |  | 
1 x 1.5 KW Drill Motors | D | 1.5 kW x 8 A/kW x 0.5 = 6A |  |  | 6
1 x 1.25 kW Fuel Pumps | F | 1.25kW x 8 A/kW |  | 10 | 
1 x 1.25 kW Fuel Pumps | F | 1.25kW x 8 A/kW x 0.5 |  | 5 | 
5 x 150 W Sodium Vapour | F | 5 x 2.8 A / Unit |  |  | 14
10 kW Welders @ 21 A | H | 1 x 21A = 21A, TWO Ф | 21 | 21 | 
10 kW Welders @ 21 A | H | 1 x 21A = 21A, TWO Ф |  | 21 | 21
10 kW Welders @ 21 A | H | 21A x 0.85 = 17.85A, TWO Ф | 17.9 |  | 17.9
Total |  |  | 445.7 | 446 | 447.3

## Slide 28: WA Electrical Requirements, Section 12
(b) Multiple installations which incorporate a
domestic installation where the minimum
current carrying capacity shall be:
Special Requirements for Installations in WA
12.2 Consumer Main
(i) Single phase = 32A
(ii) Multiphase = 63 A per phase

## Slide 29: WA Electrical Requirements, Section 5 Underground Supply
5.3 Types of Cables and Enclosures
Cables shall be installed in a heavy duty non metallic enclosure.
Enclosures shall comply with AS 2053 and be installed a minimum 500 mm below finished ground level

## Slide 30: AS 3008.1.1- 2009
Using Table 3 (4 )
Installation methods for cables enclosed in Underground Wiring Enclosures.
Item 4
One Three Core Cable
Table 13 - Columns 25, 26 & 27

## Slide 31: AS 3008.1.1- 2009
Cable is Four Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.
Table 13
Current carrying Capacity of Three Core, Sheathed cables with or without earth core, armoured or un armoured, including neutral screened cables..
Highest Maximum Demand = 447 Amps
Column 25, States Cu (Copper Cables) Closest cable is 400 mm2 at 468 Amps.

## Slide 32: Installation of Consumer Mains
Highest Maximum Demand = 447 Amps
Cable required is a 400 mm2 ( 468 Amps ) Three Core TPS installed in Heavy Duty Conduit 500 mm below Finished Ground Level.

## Slide 33: This is not the only solution
Table 3 (4 ) Installation Methods for Cables in Underground Wiring Enclosures
Item 2 Three Single Core Cables
Table 7 & 8 Columns 24 & 26

## Slide 34: AS 3008.1.1- 2009
Cable is Four Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.
Table 6
Current carrying Capacity of Three Single Core, Sheathed cables with or without earth core, armoured or un armoured, including neutral screened cables.
(Benefits its much easier to bend and move)
Column 24 Cu (Copper Cables ) 445 Amps
Closest cable is 400 mm2 at 492 Amps.

## Slide 35
End of Show This has been a G I Luff Production for the use of the Electrical Trades.