## Slide 1: 3 Phase Motor Starters
Click the left mouse button for each slide
The purpose of this presentation is to describe the principles of 3-phase non-electronic current limiting starters.
Electrical Trades
Continue
3 Phase Motor Starters.pps S. G. Brooks Version 3 12/2007

## Slide 2: 3-Phase Motor Characteristics
Continue
A 3-phase squirrel cage induction (SCI) motor draws a high current and produces maximum torque when it is started direct-on-line (DOL).
The starting current is much higher than the full load current
Full load current.

## Slide 3: Typical 3-Phase SCI Motor Connections
Continue
STAR
6-terminal terminal block.
DELTA
415 V 50 Hz
415 V 50 Hz
In each case the motor must be designed for that connection on full load.

## Slide 4: Internal Motor Connections
Continue
STAR
3-terminal terminal block.
DELTA
415 V 50 Hz
In many cases the motor is internally connected in either star or delta, with a 3-terminal terminal block.
or

## Slide 5: 3-Phase DOL Starting
Continue
Direct-on-line (DOL) starting is equivalent to starting the motor with a triple-pole switch.
Motor-rated HRC fuses are required to withstand the high inrush current during starting.
Motor overtemperature protection not shown
DOL starting gives maximum starting current and maximum starting torque.

## Slide 6: 3-Phase DOL Starting With a Contactor
Continue
Direct-on-line (DOL) starting is usually achieved with an electromagnetic contactor circuit.
DOL starting gives maximum starting current and maximum starting torque.

## Slide 7: Reducing Starting Current
Continue
Each method results in a reduction in starting torque.
Reducing the starting current of an SCI motor can be achieved by:
a. Changing the stator connections during starting (using a star-delta starter).
b. Reducing the line voltage with an autotransformer during starting (using an autotransformer starter).
c. Reducing the line current with series resistors during starting (using a primary resistance starter.

## Slide 8: Star-Delta Connection
Continue
The voltage across each phase winding is reduced to 240 V during starting.
A 3-phase SCI motor that has been designed to run in delta on full load can be temporarily connected in star to reduce the current during starting.
415 V 50 Hz
STAR
DELTA
415 V 50 Hz
START
RUN
The voltage across each phase winding is 415 V for running.

## Slide 9: Typical Star-Delta Starter Power Circuit
415 V 50 Hz
Star must drop out before Delta comes in.
The Star and Line contactors come in for starting.
Star drops out and Delta comes in for running.
Continue

## Slide 10: Typical Star-Delta Starter Control Circuit
Continue
415 V coils
Start button
Star
Timer
Delta
Line

## Slide 11: Typical Automatic Star-Delta Starter
Continue
Start button
Contactor
Star point
Stop button
Overload reset
Timer
Overload relay

## Slide 12: Star-Delta Starter Characteristics
Continue
A star-delta starter reduces the line current to 33% of the DOL current, and reduces the starting torque to 33% of the DOL torque.
A star-delta starter can only be used to start motors on light starting loads (such as centrifugal pumps or air circulating fans).
A standard star-delta starter momentarily disconnects the motor during the transition from start to run.
A star-delta starter requires a 6-terminal SCI motor that is designed to run in delta on full load.

## Slide 13: Star-Delta Starter Connections
Continue
3 line terminals
6 motor terminals
6 motor cables (plus earth)
Coils may be 415 V to avoid running a neutral
Cable size can be 58% of line cables
AS/NZS 3000:2000 Clause 2.8.3.5

## Slide 14: Overloads and Single Phasing
Continue
Thermal overload heaters should be connected in the motor coil circuit, and set to the maximum coil current (not the line current) to provide ‘single phasing’ protection.
Overload heater
Overload heater
This arrangement may not provide protection against the loss of one phase.

## Slide 15: 3-Phase Autotransformer
Continue
A 3-phase autotransformer starter reduces the line current by reducing the voltage applied to the motor during starting.
3-coil autotransformer
3-terminal SCI motor (star or delta)
2-coil autotransformer
415 V 50 Hz
415 V 50 Hz
Motor starting torque is proportional to the square of the applied voltage.
80% line voltage gives 64% of DOL starting torque.
Open-delta connection
Star connection

## Slide 16: Autotransformer Starter Power Circuit
Continue
3-coil autotransformer
Start with autotransformer on 64%, then switch to DOL.

## Slide 17: Autotransformer Starter Control Circuit
Continue
Start button

## Slide 18: Autotransformer Starter Characteristics
Continue
An autotransformer starter on an 80% starting setting reduces the line current to 64% of the DOL current, and reduces the starting torque to 64% ( 0.8 2 ) of the DOL torque.
An autotransformer starter can be used to start motors on heavy loads (such as compressors, conveyors and refrigeration units).
An autotransformer starter requires a 3-terminal SCI motor.

## Slide 19: Autotransformer Starter Connections
Continue
3 line terminals
3 motor terminals
3 motor cables (plus earth)
Coils may be 415 V to avoid running a neutral
Cables same size as line cables

## Slide 20: Primary Resistance Starter
Continue
A 3-phase primary resistance starter reduces the line current by connecting resistors in series with the motor during starting.
High power resistors
3-terminal SCI motor (star or delta)
415 V 50 Hz
415 V 50 Hz
50% line voltage gives 25% of DOL starting torque.

## Slide 21: Primary Resistance Starter Power Circuit
Continue
3-terminal SCI motor (star or delta)
415 V 50 Hz
Motor starting torque is proportional to the square of the applied voltage.
Start with L in, then switch in A.

## Slide 22: (FIND THE FAULTS IN THE CIRCUIT) Primary Resistance Starter Control Circuit
Continue
415 V 50 Hz
Start button

## Slide 23: CORRECT CIRCUIT Primary Resistance Starter Control Circuit
Continue
Start button

## Slide 24: Typical Primary Resistance Starter
Continue
A primary resistance starter has one or more sets of 3 high power resistors.
Contactors
Overload relay
Timer
Stop-start station not shown

## Slide 25: Primary Resistance Starter Characteristics
Continue
A primary resistance starter on a 50% starting setting reduces the line current to 25% of the DOL current, and reduces the starting torque to 25% ( 0.5 2 ) of the DOL torque.
A primary resistance starter can can only be used to start motors on light starting loads (such as centrifugal pumps or air circulating fans).
A primary resistance starter requires a 3-terminal SCI motor.
A primary resistance starter can have several steps to increase the speed gradually.

## Slide 26: Primary Resistance Starter Connections
Continue
3 line terminals
3 motor terminals
3 motor cables (plus earth)
Coils may be 415 V to avoid running a neutral
Cables same size as line cables

## Slide 27: Secondary Resistance Starter Characteristics
Continue
For starting HEAVY loads you require a Secondary Resistance starter.
When the rotor resistance is equal to the rotor inductive reactance maximum torque is produced. With the introduction of external resistances into the wound rotor circuit, the rotor resistance and impedance values can be adjusted to produce maximum torque at the same time will minimise starting currents.
Requires a wire Wound rotor though.

## Slide 28: Useful References
Continue
1. Electrical Principles for the Electrical Trades, J. R. Jenneson, 5th Ed:
Section 13.5 - ALTERNATING CURRENT MOTOR-STARTER CIRCUITS
2. Electrical Trade Principles, J. Hampson:
Page 255 - Starter operations and applications
3. AS/NZS 3000:2000: Clauses 2.8.3.5 and 4.3.4

## Slide 29: The End
That is the end of this presentation.
3 Phase Motor Starters
Thank you for your participation.
Continue