## Slide 1: PROTECTIVE EARTHING SYSTEMS AS/NZS 3000:2007
(Or press the SPACEBAR or ENTER key)
The purpose of this presentation is to outline the general principles associated with the multiple earthed neutral (MEN) protective earthing system.
Click the left mouse button for each slide

## Slide 2: Protective EARTHING SYSTEMs
There are three general systems of earthing used in different countries only the MEN is covered by the AS/NZS 3000.
1. The MEN (Multiple Earthed Neutral)
2. The Direct Earthing system or TT or TN-S earthing System.
3. The Voltage operated ELCB

## Slide 3: REASONS FOR AN EARTHING SYSTEM
An earthing system is a safety feature of an electrical installation.
An earthing system provides:
    protection against electric shock hazards
    protection against electrically initiated fires
    voltage stability
    correct functioning of equipment.

## Slide 4: REASONS FOR AN EARTHING SYSTEM (Cont)
Fault currents or standing leakage currents in an unearthed electrical system may cause the electrical potential of the system to ‘float’.
Connection of the neutral conductor to the earthing system provides a stable electrical potential with respect to earth.
This ensures that electrical equipment has the correct applied voltage.

## Slide 5: The MEN EARTHING System
Continue
In the multiple earthed neutral (MEN) system the parts of the installation which are required to be earthed are connected to the general mass of earth within the installation (via a main protective earthing conductor), and, in addition, are connected within the installation to the neutral conductor of the supply system at one point - the main neutral link (see Wiring Rules, Clause 1.4.66).
The neutral is also earthed at the supply authority's distribution transformers and sub-stations.

## Slide 6: The MEN EARTHING System ( cont)
Continue
The MEN earthing system includes:
    the main earth terminal
    the main earthing conductor
    the earth electrode
    the MEN connection
    protective earthing conductors
    equipotential bonding conductors
    functional earthing conductors.

## Slide 7: The MEN EARTHING System (cont)
Continue
The MEN system is a current-operated system. Circuit protection devices disconnect the supply in the event of an over-current.
The impedance of the current path must be low enough to ensure that the protection device will operate.

## Slide 8: MEN earthing Outline Diagram
Continue
The installation main neutral link is connected to the general mass of earth:

## Slide 10: Advantage of the MEN earthing System
Continue
The main advantage of the MEN system is that the neutral is connected to the earth at every distribution centre and installation in the supply system, thus providing many parallel paths for any fault currents.
The MEN system is the system used in most installations in W.A.
The main disadvantage is that the resistance of the earthing conductors and earthing circuits must always be low enough to ensure that sufficient current can flow under fault conditions to allow the protection device to operate within a specified time (see AS/NZS 3000 Clause 1.7.4.3.3). The Wiring Rules require that the resistance of a main earthing conductor must not exceed 0.5 ohms (see Clause 6.3.3).

## Slide 11: Operation of the MEN earthing System
Continue
The operation of an MEN earthing system depends mainly on there being an adequate conducting path between the neutral conductor and the general mass of earth.
The supply is automatically disconnected when sufficient current flows in the circuit to operate the circuit protection device such as a fuse or circuit breaker, thus providing protection against electric shock in case of a fault.

## Slide 12: Automatic Isolation
Continue
If the earthing conductor was correctly connected a high current would flow from the outer casing to earth via the earth in the socket outlet and the circuit protection device (fuse or circuit breaker) protecting the circuit would operate and automatically isolate the circuit from the supply.
Earth Fault

## Slide 13: Fault Condition
Continue
If the earthing conductor was not connected, or if it was not able to carry the current required to operate the circuit protection device, or the resistance of the earthing circuit was too high, the outer metal casing would remain alive; any person touching the frame while in contact with any earth would suffer an electric shock.
Earth Fault

## Slide 14: Men Earth faults
Continue
Faults that affect the operation of an electrical installation include:
    open circuit supply neutral
    reversed polarity of the supply
    mistakes in wiring
    neutral to earth breakdown.

## Slide 15: Men Earth faults
Continue
The supply neutral conductor normally carries out-of-balance currents and under fault conditions it carries the fault current.
A high-resistance connection or an open circuit in the neutral conductor could place the electrical installation in a potentially dangerous condition.

## Slide 16: Men Earth faults
Continue
Even though an open circuit neutral may present a dangerous situation, the advantages of the MEN system are deemed to outweigh the disadvantages.
Reversed polarity of the supply should not happen if correct procedures are followed.

## Slide 17: Limitations
Continue
Earthing an appliance does not provide protection against electric shock if a person touches the active and neutral or active and earth simultaneously.
Earthing an appliance does not prevent faults from occurring, nor does it correct any faults; it limits the touch voltage and removes the supply from the faulty section of the circuit

## Slide 18: Disconnection Times
Continue
Clause 1.5.5.3 of AS/NZS 3000 specifies the disconnection times for a 230/240 volt supply voltage as:
0.4 seconds for final subcircuits that supply
socket outlets having rated currents less than 63A or
Hand held Class 1 equipment or
Portable equipment intended for manual movement during normal use
5 seconds for other circuits including submains and final subcircuits supplying fixed or stationary equipment.

## Slide 19: Requirements for Earthing
Continue
The main requirements for earthing are contained in Section 5 of the Wiring Rules.
Typical samples of the requirements are given in the slides which follow.

## Slide 20: Cable Colour
Continue
The only permissible colour for an insulated earthing conductor is green/yellow

## Slide 21: Insulation Resistance
Continue
The condition in which the resistance between any part of circuit and the exposed metal frame of an appliance (i.e. the insulation resistance) is below specified limits is known as an 'earth fault' or low insulation resistance to earth. The same term is applied to complete installations.
The insulation resistance between all live conductors connected together and earth must not be less than 1 megohm, measured with a high voltage insulation tester (Megger), and with all protective devices in circuit and all switches on (individual consuming devices may be disconnected).

## Slide 22: Make First - Break Last
Continue
Where a portable single insulated appliance is supplied by a flexible cord, and is connected to the supply via a plug and socket-outlet, provision must be made for the earthing pin to automatically make contact first and break contact last.
This is achieved by making the earth pin in the plug-top longer that the other pins.

## Slide 23: Incorporation of Earthing Conductor
Continue
If a portable single insulated appliance is supplied by a flexible cord the earthing conductor must be incorporated in the same outer sheath as the associated live conductors
It is not permissible to supply a single insulated appliance using two core flexible cord, and tape an additional conductor to the outside of the sheath of the flexible cord and use it as an earthing conductor.

## Slide 24: Exposed Conductive Parts
Continue
The conditions under which a protective earthing conductor may be connected to exposed conductive parts such as a constructional bolt are contained in AS/NZS 3000
It is not permissible to connect an earthing conductor to structural or ornamental metallic framework which does not form an integral part of an appliance.

## Slide 25: Earthed Situation
Continue
An 'earthed situation' is a situation wherein there is a reasonable chance of a person touching the exposed metal of an appliance and, at the same time, coming in contact with an earth

## Slide 26: Soldered Joints
Continue
Joints in copper main earthing conductors up to 16 square mm are usually soldered.
Soldered joints must be made so that the earthing conductors are retained in position independent of the solder

## Slide 27: Equipotential Bonding
Continue
Equipotential bonding is the process of connecting metallic water piping, waste pipes and other extraneous metal in contact with the ground and accessible to personal contact, with the earthing system of the electrical installation
They are intended to minimise unwanted voltages between accessible metallic parts of electrical equipment and accessible metallic parts which are not part of the electrical installation.
Equipotential bonding conductors are treated in the same way as earthing conductors.

## Slide 28: Insulation Classifications
Continue
Most low voltage electrical appliances are manufactured to one of three general insulation specifications, namely:
Single Insulated (Class I equipment)
Double Insulated (Class II equipment)
All Insulated

## Slide 29: Single Insulated (Class I)
Continue
Single Insulated
In a single insulated appliance there is one layer of insulation between the internal live components and the outer metal enclosure.

## Slide 30: Double Insulated (Class II)
Continue
Double Insulated In a double insulated appliance there are two layers of insulation between the internal live components and the outer metal enclosure; the layers of insulation are called the functional layer and the protective layer.
The international symbol to indicate double insulation is one square inside another.
Double insulated appliances must NOT have exposed metal connected to earth, and they have a warning label such as 'DO NOT EARTH - DOUBLE INSULATED'. See AS/NZS 3000 Clause 1.4.26 (Class II equipment)

## Slide 31: All Insulated
Continue
All Insulated
All insulated appliances have no exposed metal parts so they do not have an earth.

## Slide 32: Single Insulated Devices
Continue
Many electrical appliances which operate at voltages exceeding 50 volts a.c. are of the single insulated type.
Single insulated devices must never be connected to the supply unless the exposed metal is connected to the general mass of earth via the earthing conductor in the flexible cord and the earthed pin in the socket-outlet.
Live terminals or parts must not be accessible to users of electrical equipment.

## Slide 33: Size of Earthing Conductors
Continue
Protective earthing conductors must be large enough to carry the current which will enable the associated circuit protection device to operate before the cables in the circuit are damaged under fault current.
Table 5.1 gives the minimum permissible earthing conductor size for a range of copper and aluminium cables.
The requirements for determining the mimimum permissible size of earthing conductors are contained in AS/NZS 3000

## Slide 34: Functional Earthing
Continue
Functional earthing is an earthing arrangement provided to ensure correct operation of electrical equipment or to permit reliable and proper functioning of electrical installations.
Functional earthing is required in the internal circuitry of some types of electronic equipment such as that used in entertainment, communications and instrumentation applications, to prevent unwanted potential differences in the equipment.

## Slide 35: The End
Thank you for participating in this presentation
Click the left mouse button to exit
(Or press the SPACEBAR or ENTER key)