## Slide 1: Testing Switchboards
Electrotechnology Practices
By Jeff Hampson
Animations by Grahame Byrnes

## Slide 2: Preface
It is a requirement of the Electricity (Licensing) Regulations 1991 that
all electrical installing work carried out in Western Australia complies
with the relevant standards, including AS/NZS 3000:2007 and WA
Electrical Requirements.
All completed electrical work must be checked and tested by a licensed
electrician before the work is certified as complying to the relevant
network operator.
This PowerPoint presentation has been produced as a guide to
meeting the checking and testing requirements. While this guide is
mainly focused on domestic installations, the principles apply to all
electrical installing work. The methods in this presentation are not
intended to be exclusive. Other methods may be used, as long as they
meet the minimum requirements of AS/NZS 3000:2007

## Slide 3: Installation Test Certificate
After the installation work is complete, a licensed electrician must carry
out checks and tests to make sure that the work meets the
requirements of the Wiring Rules.
Once the work is confirmed as correct, a Notice of Completion is
supplied to the network operator, a Safety Certificate to the client and a
Installation Test Certificate is fixed inside the meter enclosure.
The electrician is requested to record some key installation test results
and the route of the consumer’s mains cable on a self adhesive label
which is also placed inside the meter enclosure.
1) Main Earth Resistance
2) Earth Continuity or Fault Loop Impedance values of each sub-circuit
3) Insulation resistance value for each sub circuit

## Slide 4: Installation Test Certificates
Preliminary/Completion Safety Certificate

## Slide 5: Checking and Testing
1) Visual Inspection - should be carried out whilst referring to a plan to ensure a systematic check to pick up any omissions and to verify that the work complies with the requirements of the applicable standards.
2) Earth Resistance and Continuity Tests - this test includes the
main earthing conductor, protective earth conductors and bonding
conductors.
3) Insulation Resistance Test - this test is necessary to ensure that the
insulation resistance between live parts/conductors and earth is
adequate.
4) Polarity Test - used to ensure correct connection of active, neutral
and earthing conductors.

## Slide 6: Checking and Testing
5) Correct Circuit Connections - this test checks earthing conductors do not carry current during normal operation and no short circuit exists.
6) Fault Loop Impedance - measures the fault loop impedance of each circuit to verify the protective device will operate.
7) Verification of RCD (residual current device) Operation - testing of RCDs is carried out to ensure that the RCD operates.

## Slide 7: 9.2 Functional blocks of an electrical installation
Submains
Final
Subcircuit
Distribution
Board
Load
Main
Board
Consumer’s
Mains
Point of
Supply

## Slide 8: Figure 9.5 Visual inspection of earthing system

## Slide 9: Figure 9.12 Measuring resistance of main earthing conductor
Disconnect Equipotential Bonding conductor

## Slide 10: Figure 9.13 Resistance test of protective earth at lighting point & fixed equipment
Disconnect Equipotential Bonding conductor
(In 3000:2007 – Pg 329, Table 8.2)

## Slide 11: Figure 9.14 Resistance test of protective earth at socket-outlet
Disconnect Equipotential Bonding conductor

## Slide 12: Figure 9.15 Resistance tests of equipotential bonding conductors
Reconnect Equipotential Bonding conductor

## Slide 13: Figure 9.16 Resistance test of conduit bonding conductor and conduit continuity

## Slide 14: Figure 9.19 Testing the impedance of the earth-fault loop of a final sub-circuit

## Slide 15: Figure 9.20 Connection test – lighting points

## Slide 16: Figure 9.21 Connection test – socket outlets

## Slide 17: Figure 9.22 Connection test – permanently connected equipment

## Slide 18: Figure 9.23a Interconnection tests between conductors of different circuits

## Slide 19: Figure 9.23b Interconnection tests between conductors of different circuits

## Slide 20: Figure 9.28 Theoretical fall of resistance around an earth electrode
0
10m
Distance (m)
20m
Resistance (ohms)
20
40
60
80
100
x
P
C