## Slide 1: DEMYSTIFYING PHASOR DIAGRAMS

## Slide 2
Points to remember
Phasor diagrams rotate anticlockwise.
Voltage phasors represented by lines with open arrows at the end of the lines.
Current phasors represented by lines with closed arrows at the end of the lines.
ORIGINAL SLIDES (AUTHOR UNKNOWN)
UP- DATED BY
CARL Y. MILLAR
PHASOR DIAGRAMS
Chart: 
CONTINUE

## Slide 3
Chart: 
PHASOR DIAGRAMS ROTATE ANTI-CLOCKWISE
PHASOR DIAGRAM
REPRESENTING THREE
PHASE VOLTAGES
415 V SUPPLY
120 DEGREES APART
VECTOR ROTATING THROUGH 120 DEGREES
CONTINUE

## Slide 4: Red Phase Current
40 amps
Power factor 0.8 lagging
Inverse cosine of 0.8
= 36.869°
Round to 37°
Decide on Scale ie: 1 amp = 1mm
Draw line lagging Red voltage line by 37°
to represent 40 amps
CONTINUE

## Slide 5
VOLTS RED
PHASE
VOLTS BLUE PHASE
VOLTS WHITE PHASE
37°
40 AMPS
( LAGGING )
LINES DRAWN TO SCALE = 1AMP = 1 MM
CONTINUE

## Slide 6: White Phase Current
50 amps
Power factor 0.85 lagging
Inverse cosine of 0.85
= 31.788°
Round to 32°
Use same scale
Draw line lagging White voltage line by 32°to represent 50 amps
CONTINUE

## Slide 7
VOLTS RED PHASE
VOLTS BLUE PHASE
VOLTS WHITE PHASE
37°
40 AMPS
( LAGGING )
32°
50 AMPS
( LAGGING )
CONTINUE

## Slide 8: Blue Phase Current
60 amps
Power factor 0.9 lagging
Inverse cosine of 0.9
= 25.841°
Round to 26°
Use same scale
lagging Blue voltage line by 32°Draw line
to represent 60 amps
CONTINUE

## Slide 9
VOLTS RED PHASE
VOLTS BLUE PHASE
VOLTS WHITE PHASE
26°
37°
32°
60 AMPS
50 AMPS
40 AMPS
CONTINUE

## Slide 10
THE PHASOR DIAGRAM NOW HAS THE THREE VOLTAGES AND CURRENTS ON IT, SO WE CAN MEASURE THE NEUTRAL CURRENT
BY PLOTTING PARALLELOGRAMS DERIVED FROM THE LINE CURRENTS.
60 AMPS
50 AMPS
40 AMPS
CONTINUE

## Slide 11
STEP 1
COMPLETE THE PARALLELOGRAM FOR THE BLUE AMPS &
THE RED AMPS
CONTINUE

## Slide 12
FINAL PLOTTING TO OBTAIN NEUTRAL CURRENT
18 AMPS
60 AMPS
40 AMPS
50 AMPS
NEUTRAL
CURRENT
CONTINUE

## Slide 13
STEP 2

## Slide 14
Step 3
draw a
parallelogram
using the
resultant
of the
first two
currents
and the
last
remaining
current.
V blue
V white
V red
STEP 3

## Slide 15
STEP 4

## Slide 16
THAT COMPLETES THIS INSTRUCTION
ON VECTOR PARALLELOGRAMS