## Slide 1
ELECTRICAL TRADES
Maximum Demand
Caravan Park

## Slide 2: Introduction
Calculate the Maximum Demand of a three phase non domestic installation using AS/NZS 3000
Determine the cable size of the consumer main from the Maximum Demand with reference to WA Requirements and AS/NZS 3008.1.1
Determine if the cable size of the consumer main from the Maximum Demand meets the requirement for volt drop with reference to WA Requirements and AS/NZS 3008.1.1

## Slide 3: Caravan Park Installation
Calculate the Maximum Demand for the following 415V installation.
Cable is Four Core, orange sheathed, TPS V75, Stranded copper , installed in Heavy Duty Conduit at 500 mm below ground level.
Valid Assumptions
The Consumers mains is 30M to the main switchboard. It has a 2V voltage drop.
All Voltage Drops to Amenities Block, Site Distribution is 1% and Pillar 6 is 3%.
Look at AS/NZS 3001.2008 for info on Amenities block and pillars max demand.
Conduits are 6 separate circuits buried 300mm apart.
Socket outlets for Heavy Duty loads(Substantial aircon and Heating use)

## Slide 5
Caravan Park

## Slide 6: AS/NZS 3000:2007, Appendix C, Table C2, Page 359
Columns 2 deals with Residential institutions, hotels, hospitals , motels etc
Columns 3 deals with Factories, shops, stores , offices schools, etc

## Slide 7: AS/NZS 3000:2007 Appendix C, Table C2, Page No 359
Caravan Park
  Determine Electrical requirements with regards to Load Groups - Column 3

## Slide 8: Site Office
Load Group | Load | Remarks | Calculations | Load Distribution Nos. Circuits |  |  | Contribution / Phase - Amps |  | 
 |  |  |  | R | W | B | R | W | B
A(i) | 2 x twin 36W fluorescents | 0.5A each | 0.5 x 2 = 1 A | 2 |  |  | 1A |  | 
B(ii) | 4 x double GPO’s (8pts) | 1A / point, Table C8, | 8 x 1A |  | 4 (8) |  |  | 8A | 
C | 1 x reverse cycle Aircon. | 12 A fixed load | 1x12A |  |  | 1 |  |  | 12A
 |  |  | Max demand sub mains |  |  |  | 1 | 8 | 12

## Slide 9
Amenities Block
 | Amenities Block | 50% of CB rating AS/NZS 3001 – A2.1 |  |  |  |  |  |  | 
 | 8 x twin 36W fluorescents | 0.5 A each | 0.5A x 8 = 4A (1 x 10A CB x 50% = 5A) | 8 |  |  | 5 |  | 
 | 10 x double GPO’s (20pts)( 7,7,6) | 2A / point, Table C8 | 1 X 7Pts x 2 = 14A = 1 x 16A x 50 % = 8A 6Pts x 2A = 12 A = 1 X 16 A x 50 % = 8A | 7 | 7 | 6 | 8 | 8 | 8

## Slide 10
Amenities Block
 | Amenities Block | 50% of CB rating AS/NZS 3001 – A2.1 |  |  |  |  |  |  | 
 | 8 x twin 36W fluorescents | 0.5 A each | 0.5A x 8 = 4A (1 x 10A CB x 50% = 5A) | 8 |  |  | 5 |  | 
 | 10 x double GPO’s (20pts)( 7,7,6) | 2A / point, Table C8 | 1 X 7 x 2 -= 14A = 1 x 16A x 50 % = 8A x 50% 6 x 2A = 12 A = 1 X 16 A x 50 % = 8A | 7 | 7 | 6 | 8 | 8 | 8
 | 6 x 3.6kW clothes dryers, @ 2 per / Ø |  |  |  |  |  |  |  | 
 | 2 x 3600W/240V = 15A (16A CB ea) | 50% of CB rating | 16A x 50% =8A, 8A x 2 =16A / Red Phase | 2 |  |  | 16 |  | 
 | 2 x 3600W/240V = 15A (16A CB ea) | 50% of CB rating | 16A x 50% =8A, 8A x 2 =16A / White Phase |  | 2 |  |  | 16 | 
 | 2 x 3600W/240V = 15A (16A CB ea) | 50% of CB rating | 16A x 50% =8A, 8A x 2 =16A / Blue Phase |  |  | 2 |  |  | 16

## Slide 11
Amenities Block
 | Amenities Block | 50% of CB rating AS/NZS 3001 – A2.1 |  |  |  |  |  |  | 
 | 8 x twin 36W fluorescents | 0.5 A each | 0.5A x 8 = 4A (1 x 10A CB x 50% = 5A) | 8 |  |  | 5 |  | 
 | 10 x double GPO’s (20pts)( 7,7,6) | 2A / point, Table C8 | 1 X 7 x 2 -= 14A = 1 x 16A x 50 % = 8A x 50% 6 x 2A = 12 A = 1 X 16 A x 50 % = 8A | 7 | 7 | 6 | 8 | 8 | 8
 | 6 x 3.6kW clothes dryers, @ 2 per / Ø |  |  |  |  |  |  |  | 
 | 2 x 3600W/240V = 15A (16A CB ea) | 50% of CB rating | 16A x 50% =8A, 8A x 2 =16A / Red Phase | 2 |  |  | 16 |  | 
 | 2 x 3600W/240V = 15A (16A CB ea) | 50% of CB rating | 16A x 50% =8A, 8A x 2 =16A / White Phase |  | 2 |  |  | 16 | 
 | 2 x 3600W/240V = 15A (16A CB ea) | 50% of CB rating | 16A x 50% =8A, 8A x 2 =16A / Blue Phase |  |  | 2 |  |  | 16
 | 6 x 15A 1Ø GPO’s, @ 2 per / Ø |  |  |  |  |  |  |  | 
 | 2 x 15A GPO’s (16CB ea) | 50% of CB rating | 16A x 50% = 8A, 8A x 2 =16A / Red Phase | 2 |  |  | 16 |  | 
 | 2 x 15A GPO’s (16CB ea) | 50% of CB rating | 16A x 50% = 8A, 8A x 2 =16A / White Phase |  | 2 |  |  | 16 | 
 | 2 x 15A GPO’s (16CB ea) | 50% of CB rating | 16A x 50% = 8A, 8A x 2 =16A / Blue Phase |  |  | 2 |  |  | 16
 |  |  | Max demand sub mains |  |  |  | 45 | 40 | 40

## Slide 12
Service Pillars
 | Service Pillars- 2 per phase | AS/NZS 3001 A2.2(b)(ii) |  |  |  |  |  |  | 
 | 8 GPO’s per phase | 60A+6A(7th)+6A(8th) = 72A | 72A per phase |  |  |  | 72 | 72 | 72
 |  |  | Max demand sub mains |  |  |  | 72 | 72 | 72
 |  | Max Demand Consumer Mains - Amps |  |  |  |  | 118 | 119 | 124

## Slide 13
Consumer's Mains
Maximum demand: 123A, 124A,126A_______
Minimum permissible size (copper): 95mm2
Type of cable: V75, 4C+E, Circular, Orange Sheath, TPS.
Calculations:
413V at Main Switchboard VD = 415 – 413 = 2V
C.C.C. T13, C25 Buried in enclosure, 50mm2,
C23, Buried direct, 35mm2 .
VC = 1000VD / L x I, VC = 1000 x 2V / 30m x126A = 0.529mV/A.M
T42, C6 – 95mm2

## Slide 14
Site Distribution Board Submains:
Maximum demand: 72A
Minimum permissible size (copper): 35mm2
Type of cable: V75, 4C+E, Circular, Orange Sheath, TPS
Installation conditions: Buried in enclosure, or Buried direct _
Calculated maximum voltage drop: 1%, - 4.13V
Calculations:
Voltage at Site Distribution Board Submains V = 413 – 4.13 = 408.87V
C.C.C. T13, C25 Buried in enclosure, 16mm2 (should go to 25 mm2)
C23, Buried direct, 16mm2 .
VC = 1000VD / L x I, VC = 1000 x 4.13V / 39m x 72A = 1.470
T42, C6 – 35mm2

## Slide 15
Amenities Distribution Board Submains:
Maximum demand: 47A
Minimum permissible size (copper): 16mm2
Type of cable: V75, 4C+E, Circular, Orange Sheath, TPS
Installation conditions: Buried in enclosure, or Buried direct _
Calculated maximum voltage drop: 1% - 4.13V
Calculations:
Voltage at Site Distribution Board Submains V = 413 – 4.13 = 408.87V
C.C.C. T13, C25 Buried in enclosure, 10mm2, C23, Buried direct,
10mm2
VC = 1000VD / L x I, VC = 1000 x 4.13V / 35m x 45A = 2.62
T42, C6 – 16mm2

## Slide 16
Site Distribution Pillar (Number 6):
Maximum demand: 40A – 3001 Clause A2.2(b)(i)
Minimum permissible size (copper): 25mm2
Type of cable: V75, 2C+E, Circular, Orange Sheath, TPS
Installation conditions: Single Circuit Buried in Separate enclosures, enclosures separated
Calculated maximum voltage drop: 3% - 7.08V
Calculations:
Voltage at Site Distribution Pillar (Number 6)
= 408.87/1.73 = 236.06V ie 3% 0f 236.06V = 7.08V
Deration Tables T26 (2) C3 = 0.82
New C.C.C. =40 / 0.82 = 48.78A,
C.C.C. T10, C25 Buried in enclosure, 6mm2
VC = 1000VD / L x I, VC = 1000 x 7.08V / 64m x 40A = 2.765 x 0.866 (1Ø - 3Ø)
New VC = 2.39
T42, C6 – 25mm2

## Slide 17
Is the Installation compliant
Consumers Mains = 95mm2
VD = 30m x 124A x 0.431mV/A.M = 1.616V
Site Distribution Board = 35mm2
VD = 39m x 72A x 1.11mV/A.M = 3.12V
Pillar 6 = 25mm2
VD = 64m x 40A x 1.54mV/A.M = 3.94V
Total Vd = 1.62V + 3.12V = 3.94V = 8.68V
Allowed 240V x 5% = 12V

## Slide 18
End of Show This has been a Geoff F-Production for the use of the Electrical Trades.