## Slide 1: Circuit Protection Principles
Circuit Protection.pps Version 3 S. G. Brooks 2006: Revised Terry O’Grady 2013
References:
AS/NZS 3000:2018 Wiring Rules
AS/NZS 3008.1.1:2017 Cable Selection
Building & Trades
Midland
This presentation outlines the principles of circuit protection in an electrical installation.
It is intended for use in the delivery of these competencies;
UEENEEG107A, UEENEEG063A

## Slide 2: Health, Safety & Environmental Message
In our day-to-day lives, it is easy to forget about our obligations to future generations and indeed, to our own not too distant future. Working sustainably is and should be one of our most important goals. We should all strive to
“Cause No Harm”.
It matters not whether you are the CEO of a large multi-national corporation or an employee in a small organisation, you have a “Duty of Care” to yourself, your work mates and the general public at large.
If you become aware of a hazardous situation that could harm a person, thing or the environment, it is your duty to report it to an authority which can act immediately. This may include, but not limited to, chemical or petroleum spills, toxic smoke, dust & fibre plumes and groundwater contamination.
There is compelling evidence that plastic materials have seriously polluted our oceans, that fertiliser run-off from agricultural activities has made our river systems nutrient-rich and that the burning of fossil fuels for energy is causing climate change. We must all strive for a “cleaner and better world”.

## Slide 3: Circuit Protection Considerations - Overview
kVA x 1000
IFL = ---------------
√3 x VLINE
IFL x 100
ISC = ----------
Z%
VPh
IFault = -----------
Z1 + Z2
Uo
Zext = -----
Ia
K2.S2
t = -------
I2
1000 x Vd
Vc = ---------------
L x I
Distribution transformer
415/240 V
500 kVA
Z% = 5%
The transformer has a full load current rating per phase IFL.
The consumers mains have impedance Z2 .
The transformer has a maximum prospective short circuit current per phase ISC.
The transformer has an impedance per phase Zext or Zint
Circuit breakers must be able to interrupt up to the prospective short circuit current within a time.
Cables have a maximum current rating.
Volt drop must not exceed 5%.
AS/NZS3008.1.1:2009 Tables
AS/NZS 3000:2009 Clause 3.4
AS/NZS 3000:2007 Appendix C2
AS/NZS 3000:2007 Appendix C4
AS/NZS 3000:2007 Clause 2.5.4.2
Click any box to find out more.
Click on the “U” to return back here
AS/NZS3000:2009 Appendix B4.4
Mains and submains have a maximum demand.
Maximum Circuit Length
AS/NZS3000:2009 Appendix B5

## Slide 4: Wiring Systems
Electrical wiring systems must be installed in such a way that safe working limits are not exceeded. One of the main considerations is the maximum safe current.
If the maximum safe current in a circuit is exceeded it can result in damage to the cable and/or associated parts of the installation.

## Slide 5: Current Definitions
AS/NZS 3000:2007 provides the following definitions relating to current:
Over-current – A current exceeding the rated value. (Clause 1.4.70)
Fault current – A current resulting from an insulation failure or from bridging of insulation. (Clause 1.4.37)
Overload current – An over-current occurring in a circuit which is electrically sound. (Clause 1.4.38)
Short-circuit current - A fault current resulting from a fault of negligible impedance between live conductors having a difference in potential under normal operating conditions. (Clause 1.4.39)

## Slide 6: Protection of Wiring
The general requirements for the protection of wiring are:
Small overloads of short duration should not cause the protection to operate.
The protection must operate, even on a small overload, and if the overload persists long enough to cause overheating of the circuit conductors.
The protection must open the circuit before damage caused by fault currents can occur.
Protection must be ‘discriminative’ in that only the faulty circuit is isolated and other circuits remain operative and unaffected.

## Slide 7: Overload Protection
Overload protection is achieved by opening the circuit before overheating or deterioration of the protected wiring can occur.

## Slide 8: Coordination Requirement
AS/NZS 3000:2007 Clause 2.5.7.2 requires coordination between conductors and protective devices. Appendix B3.2 provides additional information.
The operating characteristics of a device protecting a cable against overload shall satisfy the following two conditions:
1. IB ≤ IN ≤ IZ
2. I2 ≤ (1.45 x IN)
Where:
IB = Circuit maximum demand.
IN = Nominal current of protective device.
IZ = Current carrying capacity of cable.
I2 = Current to operate protective device:
1.45 x IN for circuit breakers or
1.6 x IN for HRC fuses.
Less than or equal to
‘Conventional time’ in
Clause 2.5.3 (a) & (b) is 1 hour
up to 63 amps and
2 hours over 63 amps.

## Slide 9: Coordination
1. IB ≤ IN ≤ IZ
2. I2 ≤ (1.45 x IN)
Where:
IB = Circuit maximum demand.
IN = Nominal current of protective device.
IZ = Current carrying capacity of cable.
I2 = Current to operate protective device:
1.45 x IN for circuit breakers or
1.6 x IN for HRC fuses.
Maximum
demand of
circuit
Nominal
current
rating of
protective
device
Continuous
current
Carrying capacity of
conductor
Operation
of circuit
breaker
Operation
of HRC
fuse
IZ
IN
IB
I2
I2
See AS/NZS 3000:2007 Clause 2.5.3.1

## Slide 10: Short-circuit Protection
Short-circuit fault protection is achieved by:
The action of the fuse or circuit breaker in being fast enough to open the circuit before the let-through energy can attain a value that would cause damage by overheating, arcing or mechanical stress; and
The protective device being capable of opening the circuit, under these high fault current conditions, without damage to itself.

## Slide 11: Short Circuit Current
In the case of a short circuit, there are two limiting factors to the magnitude of the current value, they are;
The circuit impedance of the fault circuit
The available short circuit energy.
This includes the impedance of the supply source, in most cases the Distribution Transformer provided by the network operator.

## Slide 12: Transformer Impedance Percent
The impedance percent of a transformer is usually stated as the percentage of the primary-rated voltage that is necessary to cause full-load current in the secondary if the load terminals have a short across them.
A distribution transformer having a full load current rating of 500 amps and an impedance percent of 5% would have a theoretical short circuit current of 20 x 500 or 10 000 amps.
A common transformer impedance percent value is 5 per cent. If 5 per cent of supply voltage will produce full load current, then,with a secondary short circuit and normal supply voltage of 100 per cent, twenty times the rated full load current will be present.
100
Short circuit current = Full load current x ------------------
Impedance %

## Slide 13: Transformer Full Load Current
The rated full load output current of a typical three-phase distribution transformer is given by the equation:
So the rated full load current of a 500 kVA, 415 - 240 volt three phase distribution transformer with an impedance of 5% is:
= 695.6 A
kVA x 1000
IFL = ----------------
√3 x VLINE

## Slide 14: Prospective Fault Current
The available short circuit current of a 500 kVA / 415 volt transformer if it had an impedance of 5% would be:
= 13 912 A
ISC = 13 912 A
500 kVA 415 V
5% Impedance

## Slide 15: Impedance/Phase of Supply
If the available short circuit current of the 415 volt 500 kVA transformer was 13 912 amps, the impedance per phase (Z1) would be:
= 0.01725 ohms
ISC = 13 912 A
500 kVA 415 V
5% Impedance
Z1 = 0.01725 

## Slide 16: Cable Impedance
The prospective fault current (fault level) per phase at the main switchboard is limited by the impedance of the supply (Z1) plus the impedance of the cables from the source to the switchboard i.e. The consumer’s mains (Z2)
The impedance of the consumers mains can be found from relevant tables if the cable size, type and length are known.
ISC = 13 912 A
500 kVA 415 V
5% Impedance
Z1 = 0.01725 
Consumers
Mains
Z2

## Slide 17: Fault Level at Main Switchboard
If the consumers mains consisted of 30 metres of 16 mm2 copper TPS cable then the impedance of the active conductor (Z2) would be approximately 0.0339 ohms per phase (from a Table). Therefore the prospective fault current level at the main switchboard would be:
= 4692 A

## Slide 18: Circuit Breaker Rating
Since the prospective fault current at the main switchboard is 4692 amps, the circuit breakers on the main switchboard need to rated at a short circuit current above this value. A rating of 8 kA would be suitable.
Circuit breaker rating = 8 kA

## Slide 19: Equation Summary
IB ≤ IN ≤ IZ
Distribution Transformer
Main Switchboard
I2 ≤ (1.45 x IZ)

## Slide 20: Fault Loop Impedance
Fault-loop impedance is the impedance of the conductors in the series path taken by the current in the event of a fault between an active conductor and Earth, starting and ending at the point of the earth fault.
AS/NZS 3000 requires that each circuit is protected such that automatic disconnection of supply occurs within a specified disconnection time when a fault of negligible impedance occurs between an active conductor and a protective earthing conductor or an exposed conductive part anywhere in an electrical installation. See Clause 2.4.2
This condition is satisfied when the fault-loop impedance is sufficiently low to allow enough current to flow in the fault-loop to cause the circuit protection device to operate within the specified time, thus limiting the touch voltage as required by Clause 1.5.5.3

## Slide 21: Fault Current Path (MEN)
See Figure B5 AS3000:2018

## Slide 22: Disconnection Times
The maximum disconnection time for 230/240 V supply voltage shall not exceed the following (See AS/NZS 3000:2007 Clause 1.5.5.3 (d)
(a) 0.4 seconds for final sub-circuits that supply;
(i) socket-outlets having rated currents not exceeding 63 A; or
(ii) hand-held Class I equipment; or
(iii) portable equipment intended for manual movement during use.
(b) 5 seconds for other circuits including sub-mains and final sub-circuits supplying fixed or stationary equipment.

## Slide 23: Circuit Breaker Mean Tripping Time
The maximum value of fault loop impedance (ZS) can be calculated for circuits protected by circuit breaker using manufacturers’ information relating to the approximate mean tripping current for the circuit breaker.
The mean tripping current for circuit breakers can be taken as:
“B” Curve = 4 times rated current
“C” Curve = 7.5 times rated current (e.g. general purpose loads)
“D” Curve = 12.5 times rated current (e.g. high inductive loads)
See AS/NZS 3000:2007 Figure B6

## Slide 24: Fault Loop Impedance Equation
The fault loop impedance (ZS) for a circuit breaker can be calculated using the following equation: AS/NZS3000:2007 Clause 8.3.9
Where the circuit protective device is an RCD, the measurement of earth fault-loop impedance is not necessary; however, it is recommended that such measurement be carried out so as to identify any abnormal circuit conditions which may be present. B4.6 Note:
UO (The nominal supply voltage)
ZS = -------
Ia (The mean tripping current)

## Slide 25: Fault Loop Impedance Calculation
A 240 volt final sub-circuit supplies a load consisting of a 10 A socket outlet protected by a 16 A, Type C, 8 kA circuit breaker. Determine the fault loop impedance (Rphe) of the circuit, if the supply is not available. Refer AS/NZS3000:2007 Clause 8.3.9.3 Table 8.2
From Table 8.2 - 1.5mm2 & 2.5mm2 Rphe 1.22Ω
See AS/NZS 3000:2007 Clause B4.5
The values from Table 8.2, which have been rounded to two decimal places, are
approximately 64% of the values given in Table 8.1. This is because of the following:
A reduction to 80% (0.8) because of a conductor temperature of 20°C.
(b) A further reduction as the length of circuits given in Table B1 were calculated using 80% (0.8) of supply voltage. The further reduction assumes that 20% of the impedance is associated with the supply transformer. This should be taken into account if in doubt.
Therefore, 0.8 × 0.8 = 0.64 (64%).

## Slide 26: Maximum Circuit Lengths - Table B1
Table B1 of AS/NZS 3000:2007 contains maximum circuit lengths, above which the impedance of the conductors will limit the magnitude of the short-circuit current to a level below that required to operate the protective device protecting the circuit in sufficient time (within 0.4 seconds) to ensure safety against indirect contact.
The maximum circuit lengths in Table B1 are based on a nominal phase voltage of 230 volts. For 240 volt circuits the maximum length can be determined by multiplying the value in the table by 1.04.

## Slide 27: Touch Voltage
AS/NZS 3000:2007 Clause 2.4.2 specifies that in the event of a fault between a live part and an exposed conductive part which could give rise to a prospective touch voltage exceeding 50 V a.c. or 120 V ripple-free d.c., a protective device shall automatically disconnect the supply to the circuit or electrical equipment concerned. Also see AS/NZS3000:2007 Clause 5.2.1
Typical circuit outline.

## Slide 28: Touch Voltage Equation
If the details of the circuit are known the touch voltage ( Vt ) can be calculated using the equation:
Where:
Vo = Voltage at protective device
ZPE = Impedance of protective earth
ZA = Impedance of active
Vo x ZPE
Touch voltage = --------------
(ZA + ZPE)

## Slide 29: Touch Voltage Calculation
An appliance is installed with a 4 mm2 copper active conductor (0.0452 ohms) and has a 2.5 mm2 earthing conductor (0.071 ohms). Calculate the touch voltage if the supply voltage is 240 volts a.c.
Vo x ZPE 240 x 0.071
Touch voltage = -------------- = ----------------------- = 147 V
(ZA + ZPE) (0.0452 + 0.071)
Approximate impedance per 10 metres

## Slide 30: Touch Voltage Limit
The circuit protection device must automatically disconnect the supply if a fault occurs which could result in a touch voltage greater than 50 V a.c. or 120 V d.c. (Wiring Rules Clause 2.4.2)

## Slide 31: Short Circuit Current
AS/NZS 3000:2007 Clause 2.5.4.5 requires that general protective devices shall be provided to interrupt any short-circuit current flowing in the conductors before such a current can cause danger due to thermal and mechanical effects produced in conductors and connections.

## Slide 32: Short Circuit Disconnect Time
For short circuits of duration up to 5 seconds the time in which a given short-circuit current will raise the conductors from the highest admissible temperature in normal duty to the limit temperature may, as an approximation, be calculated from the following equation:
See AS/NZS 3008.1.1:2009 Clause 5.3 Table 52
AS/NZS 3000:2007 Clause 2.5.4.5 (b)
Where
t = duration in seconds
K = a factor dependent on the material of the conductor, the insulation and the initial and the final temperatures. See AS/NZS 3008.1.1 :2009 Table 52. A typical value of K is 111.
S = cross-sectional area of the conductor in mm2
I = effective short-circuit current (A r.m.s)

## Slide 33: Short Circuit Current
An equation to calculate the current required to disconnect the circuit in a given time can be determined by transposition:
Where
t = duration in seconds
K = a factor dependent on the material of the conductor, the insulation and the initial and the final temperatures. See AS/NZS 3008.1.1 Table 51. A typical value of K is 111.
S = cross-sectional area of the conductor in mm2
I = effective short-circuit current (A r.m.s)
so

## Slide 34: Overload Current Calculation
A single phase final sub-circuit supplies a 415 volt welding transformer from a 4 mm2 V75 TPI copper active conductor with a 2.5 mm2 copper protective-earth conductor. Determine the maximum overload current that could flow in the circuit if the associated 32 A, Type D, 8 kA circuit breaker is to operate within 4.5 seconds. The ambient temperature is 40 degrees C.
= 209.3 amps
See AS/NZS 3008.1.1:2009 5.3

## Slide 35: Maximum Demand - Purpose
Maximum demand is the name given to the maximum current likely to be drawn by an entire installation (or part thereof) for the purposes of determining the cable size and protection requirements.
Maximum demand in the mains and sub-mains of an installation is not the sum of the current which would be flowing if all circuits were loaded to their maximum, because it is unlikely that all of the devices would be switched on at the same time.

## Slide 36: Maximum Demand - Methods
The maximum demand of consumer’s mains and sub-mains can be determined four (4) ways as described in
AS/NZS 3000:2007 Clause 2.2.2
By calculation (See AS/NZS 3000:2007 Appendix C2).
By assessment (typically by the network operator).
By measurement, using a maximum demand indicator.
By limitation, using a circuit breaker with a lower current rating.
The maximum demand of final sub circuits are different - it is usually the current rating of the protective device for the circuit.
See AS/NZS 3000:2007 Clause 3.4.1 Table C5 & C6

## Slide 37: Maximum Demand - Calculations (Single Phase)
Calculation of maximum demand in mains and sub-mains requires the use of different Tables in AS/NZS 3000:2007, depending on whether the installation is domestic or non-domestic (See Tables C2.3 and C2.4).
For the purposes of calculating the maximum demand in mains and sub-mains, each type of load is classified in a 'Load Group' - see above
The process of calculating maximum demand for single phase mains and sub-mains involves grouping the given loads into the categories in Tables above and applying the relevant factors to each in determining the maximum demand currents.

## Slide 38: Maximum Demand - Calculations (Multiphase)
In multiphase installations each phase must be considered separately (Clause C4). The maximum demand of mains and sub-mains for each phase is the sum of the currents in each load group. The total calculated maximum demand is the current in the highest loaded phase.
In multiphase installations the allocation of loads to phases depends on the technical judgment of the person doing the calculation, but they should aim to use the smallest conductors possible by balancing the loads across each phase.
The size of the cable to be used for the supply mains is the minimum size cross-sectional area conductor which has the required current carrying capacity under the given installation conditions, or the minimum specified in AS/NZS 3000, whichever is greater.

## Slide 39: Maximum Demand - Calculations Table
In order to calculate maximum demand it is desirable to show the contributing load groups in a table.
When preparing a maximum demand table the loads should be arranged in the order in which they appear in the relevant table in AS/NZS 3000 and all calculations should be shown - to make it easier to check.
It is essential to read the footnotes to the table in AS/NZS 3000 where applicable. Appendix C of AS/NZS 3000 gives samples of maximum demand calculations.

## Slide 40: Maximum Demand - Single Phase Example 1
Example 1 Calculate the maximum demand for the following single phase 240 volt single phase domestic installation.
36 indoor lighting points
2 single 10 amp general purpose socket outlets
12 double 10 amp general purpose socket outlets
2 ceiling mounted exhaust fans (60 W each)
1 15 A socket outlet for a dishwasher
1 9 kW single phase cooking range
1 3.6 kW single phase storage water heater

## Slide 41: Maximum Demand Table - Sample 1
This is what a typical maximum demand calculation table for consumers mains may look like, using the given installation details:

## Slide 42: Cable Selection Factors
When the maximum demand has been calculated the cable can be selected having regard for factors such as..
a. The installation conditions.
b. The type of enclosure.
c. The ambient temperature.
d. The maximum temperature rating of the cable insulation.
e. The presence of thermal insulation materials.
f. How the cables are grouped.
g. The voltage drop in the circuit.
h. The type of material used as the conductor.
i. The type of protection provided for the circuit.
j. Regulatory requirements applying to the specific types of installations.
l. The short circuit performance of the cable under fault conditions.
m. Other external influences on cables, such as depth of laying,
thermal resistivity of soil and effects of direct sunlight.
Refer to AS/NZS3008.1 for Cable Selection criteria

## Slide 43: Permissible Voltage Drop
Wiring Rules Clause 1.8.4 requires that the volt drop between the point of supply and any point of a 240 or 415 volt installation shall not exceed 5% of the nominal supply voltage.
Since 5% of 240 is 12 volts, this means that the phase to neutral voltage measured at any point in the installation must never be less than 228 volts (i.e 240 minus 12 = 228) while the circuit current is flowing.
In a three phase circuit 5% of 415 V is 20.75 V, so the minimum permissible phase to phase voltage at any point is 415-20.75 or 394.25 V.
In an extra-low voltage circuit, the maximum allowable voltage drop is 10% - see AS/NZS 3000 Clause 7.7.7.

## Slide 44: Voltage Drop Calculations
AS/NZS 3008.1.1 Section 4 contains information on how to determine the minimum permissible size conductor for a specific run without exceeding the maximum permissible voltage drop. AS/NZS 3008.1.1 provides a detailed treatment using several different methods.
The mV/A.m method of determining voltage drop in AS/NZS 3008.1.1 (Clause 4.2) is the only method required for this presentation. The same basic process can be applied to consumers mains, sub-mains or final sub-circuits.

## Slide 45: Voltage Drop in mV/A.m
The calculations in AS/NZS 3008.1.1 (Clause 4.2) are based on a special unit called Vc which is the voltage drop in millivolts per ampere metre (mV/A.m).
Values of Vc are given for single and three phase circuits in tables of current carrying capacities in both Standards. The value of Vc for a specific circuit is found using the equation:
1000 Vd
Vc = -------------
L x I
Where:
Vc = the voltage drop over the route length of the circuit in millivolts per ampere metre (mV/A.m).
Vd = the actual voltage drop, in volts.
L = the route length of the circuit, in metres.
I = the maximum demand current in the cable in amps.

## Slide 46: Meaning of Vc (mV/A.m)
In general, selecting a suitable cable for a given circuit involves calculating the value of Vc, then looking up the appropriate tables and selecting a cable which has a value of Vc which is equal to or less than the calculated value.
It is usually useful to draw a simple line diagram of the circuit and insert the known values before you begin a calculation.

## Slide 47: Sample Calculation of Vc (mV/A.m) (Volt Drop)
Sample: A single phase circuit is to be buried direct in the ground and protected by a circuit breaker. If the route length of this circuit is 30 metres and the maximum demand is 10 amps, what is the smallest V90 TPS cable which could be used?
1000 Vd
Vc = -----------
L x I
1000 x 12
= --------------
30 x 10
So Vc = 40 mV/A.m
(Single phase)
In this sample the smallest permissible cable is one which will have a Vc equal to or less than 40 mV/A.m. From AS/NZS 3008.1.1 Table 42, 1.5 mm2 cable has a three phase Vc of 30 mV/A.m at the maximum permissible operating temperature of the cable.
The circuit in this example is single phase so this single phase Vc has to be converted to a three phase Vc by multiplying it by 0.866 (see Note in AS/NZS 3008.1.1 Clause 4.2). So Vc = 40 x 0.866 = 34.64 mV/Am. Since this is the cable which has a Vc nearest to but less than 34.64 mV/A.m, it would be suitable.

## Slide 48: Sample Calculation of Vc (mV/A.m)
1.5 mm2 cable is within the allowable limits for voltage drop, but the current carrying capacity for the given installation conditions must be checked to ensure that it is adequate.
From AS/NZS 3008.1.1 Table 9 Column 14, 1.5 mm2 cable has a current carrying capacity of 27 A. This is greater than the maximum demand of this circuit (10 A), so the cable is acceptable.
1.5 mm2 copper cable satisfies volt drop and current carrying capacity requirements.

## Slide 49: Sample Calculation of Vc (mV/A.m)
AS/NZS 3008.1.1 provides tables of the current carrying capacity and Vc for various sizes of cables. If the Vc, length and maximum demand current are known the basic equation can be transposed to calculate the actual voltage drop for a given circuit.
Similarly, other values such as length and demand current can be calculated if the other appropriate values are known. The relevant equations are given below:
1000.Vd Vc x L x I 1000.Vd 1000.Vd
Vc = ---------- Vd = -------------- L = ------------ I = ------------
L x I 1000 Vc x I Vc x L

## Slide 50: Volt Drop in an Installation
In some cases, it may be necessary to calculate the total voltage drop across the entire installation, in which, will include the consumer's mains, a sub-mains and a final sub-circuit. Under these conditions, it is necessary to determine the voltage drop occurring within each part of an installation.
Consumer's Mains Sub Mains Final SC
| ----- ---- ------
*-/--------------| MSB |-/----------| DB |-/----------| LOAD |
| 240 V ----- ---- ------
|
70 A 40 A 15 A
16 mm2 6 mm2 1.5 mm2
10 metres 25 metres 15 metres
The value of Vc for each cable can be determined using Table 42 of AS/NZS 3008.1.1 and applying the relevant conversion factor, so the maximum voltage drop at each stage can be calculated as follows :

## Slide 51: Installation Volt Drop
Consumer's Mains (16 mm2 cable). Vc = 2.43 x 1.155 = 2.806 mV/A.m)
Vc x L x I 2.806 x 10 x 70
Vd = ---------- Vd = --------------- = 1.964 V
1000 1000
Sub-mains (6 mm2 cable). Vc = 6.49 x 1.155 = 7.496 mV/A.m)
Vc x L x I 7.496 x 25 x 40
Vd = ---------- Vd = ------------- = 7.496 V
1000 1000
Final subcircuit (1.5 mm2 cable). Vc = 28.6 x 1.155 = 33.033 mV/A.m)
Vc x L x I 33 x 15 x 15
Vd = ---------- Vd = ------------- = 7.425 V
1000 1000
-------------
Total Voltage Drop = 16.885 volts
This calculation shows that
the total volt drop
across the entire circuit is 16.885 volts.

## Slide 52: Volt Drop Not Permissible
The total calculated voltage drop in this installation is above the maximum permissible value of 12 volts, therefore this configuration will not be permitted.
The most practical way to reduce the volt drop is to increase the size of cable in one of the circuits.
Increasing the size of the cable in the final sub-circuit to 4 mm2 would reduce the volt drop in the sub-circuit, thus reducing the overall volt drop to a permissible value.

## Slide 53: Reference Summary
AS/NZS 3000 Clause 2.4.4.1 General (Protection devices).
AS/NZS 3000 Clause 1.7 Protection for safety
AS/NZS 3000 Clause 1.4.34 Fault current.
AS/NZS 3000 Clause 1.4.35 Overload current.
AS/NZS 3000 Clause 1.4.36 Short circuit current 2.4.3.2.
AS/NZS 3000 Clause 2.4.3.2 Coordination between conductors and protective devices.
AS/NZS 3000 Clause B4.5 Calculation of fault loop impedance.
AS/NZS 3000 Clause Table B5.1 Maximum circuit lengths.
AS/NZS 3008.1.1 Table 51 Values of constant K.
Australian Electrical Wiring, Vol 2, Pethebridge and Neeson, 6th Ed, McGraw-Hill
AS/NZS 3000 Clause 1.4.87 Touch voltage.

## Slide 54: Test Before You Touch
Electrical accidents can be prevented by adopting safe working practices.
Two of the guiding principles which must be adopted by any electrical worker are:
TEST BEFORE YOU TOUCH
ALWAYS CHECK THE CHECKER

## Slide 55: Question 1
B. 100
ISC = IFL x ------
Z%
Select an answer
Which of the following equations is used to calculate the impedance of a typical 3 phase distribution transformer if the secondary short circuit current is known?
A. kVA x 1000
IFL = ----------------
√3 x V
C. VPHASE
ZPHASE = --------
ISC
K2 . S2
D. t = ---------
I2

## Slide 56: Question 2
Select an answer
What term is used to describe the maximum current that may flow in an electrical installation during a short circuit?
A. Prospective fault current.
B. Let-through current.
C. Cut-off current.
D. Trip or fusing current.

## Slide 57: Question 3
The supply authority fault level at the consumer’s terminals of a 240/415 volt installation is given as 15 kA. The 50 mm2 copper consumers mains are 25 m long. Calculate the theoretical fault current at the main switchboard if the cables are operating at 20º C. The mains cable resistance is 3.79 x 10-4 ohms/metre.
Answer: 6.87 kA fault current.
Click to display a typical correct answer
vs
ZSOURCE = ----
Ia
240
= ---------
15 000
= 0.016 ohms
vs
IFAULT = ----------
ZSOURCE + ZMAINS
240
= ------------------
0.016 + 0.0186
= 6870 A
ZMAINS = L x (ZACTIVE + ZNEUTRAL)
= 25 x (3.79 x 10-4 + 3.79 x 10-4)
= 0.01859 ohms

## Slide 58: Question 4
What are two of the most important precautions you can take to avoid an unwanted electric shock when working on electrical equipment?
Answer: Test before you touch and check the checker.
Click to display a typical correct answer

## Slide 59: Question 5
What is a fault current according to the Wiring Rules?
Answer: A current resulting from an insulation failure or from bridging of insulation. (AS/NZS 3000 Clause 1.4.34)
Click to display a typical correct answer

## Slide 60: Question 6
A circuit protection device must automatically disconnect the supply if a fault occurs which could result in a touch voltage greater than ……………… ?
Answer: 50 V a.c. or 120 V d.c. (AS/NZS 3000 Clause 1.7.4.3.2)
Click to display a typical correct answer

## Slide 61: Question 7
The impedance of a transformer is usually stated as the percentage of the ………?………. that is necessary to cause full-load current in the secondary if the load terminals have a short across them.
Answer: Primary-rated voltage.
Click to display a typical correct answer

## Slide 62: Question 8
Which Clause in AS/NZS 3000 specifies the requirements for co-ordination between conductors and protective devices.
Answer: AS/NZS 3000 Clause 2.4.3.2 .
Click to display a typical correct answer

## Slide 63: Question 9
What would be the most suitable type of circuit protection device for a 50 amp sub main in a commercial office block?
Answer: A circuit breaker or HRC fuse.
Click to display a typical correct answer

## Slide 64: Question 10
Select an answer
What is an overload current?
A. A current caused by a short circuit between active and earth.
B. An over-current in an electrical circuit that is faulty.
C. A current caused by a short circuit between active and neutral.
D. An excessive current in a circuit that is electrically sound.

## Slide 65: Question 11
Select an answer
What is the most important factor to consider to ensure that the circuit protection device only isolates the faulty circuit?
A . The current rating is correctly determined to protect the circuit cables.
B. Correctly graded discrimination.
C. The fault current rating matches the prospective fault current.
D. The category of the device matches the load factor.

## Slide 66: The End
Thank you for participating in this presentation.