## Slide 1
G063A Work Sheet 3
The purpose of this presentation is to provide you with the opportunity to answer the 35 questions from Work Sheet 3 of G063A .
Click the left mouse button for each slide
(Or press the SPACEBAR or ENTER key)
Version 1 CPS 2011
Protection Device Principles.pps
Unit Title: G063A – Select and Arrange Equipment for General Electrical Installations
Protection Device Principles

## Slide 2: Question 1
Continue
What part of a motor circuit are fuses designed to protect?
Answer:
Fuses are designed to protect the circuit conductors.

## Slide 3
Continue
Question 2
What diameter fuse wire has a current rating of 16 amps?
Answer:
0.5mm

## Slide 4
Continue
Question 3
What does the abbreviation HRC stand for when applied to fuses?
Answer:
High Rupturing Capacity

## Slide 5
Continue
Question 4
What are two advantages of an HRC fuse compared to semi-enclosed rewireable fuses?
Answer:
An HRC contains the disconnection arc; it is more accurate; it interrupts the circuit quicker under severe fault conditions; they do not deteriorate with age.

## Slide 6
Continue
Question 5
Why is it dangerous to temporarily replace an HRC cartridge with a length of fuse wire of the same current rating?
Answer:
An explosion could result if a short circuit occurs.

## Slide 7
Continue
Question 6
What is the most important action to take before replacing any blown fuse element (assuming that the power has been switched off)?
Answer:
Rectify the fault which caused the fuse element to blow.

## Slide 8
Continue
Question 7
What voltage would be indicated if a voltmeter was connected in parallel with a blown fuse, immediately after the fuse had blown due to a temporary severe overload (if all switches are still in the ON position)?
Answer:
The full line voltage (e.g. 240 volts)

## Slide 9
Continue
Question 8
At what approximate current would a 10 amp semi-enclosed rewireable fuse ‘blow’ if the load current was increased gradually?
Answer:
At 1.7 to 2 times the rating of the fuse element.

## Slide 10
Continue
Question 9
List two possible sources of overvoltage in a 3 phase electrical installation.
Answer:
Lighting and switching of large machinery
(e.g. Heavy loads)

## Slide 11
Continue
Question 10
What effect does it have on the rupturing time of an HRC fuse as the fault current increases?
Answer:
As the fault current increases the rupturing time decreases.

## Slide 12
Continue
Question 11
At what approximate current would a 100 amp HRC fuse interrupt the circuit if the load current was increased gradually?
Answer:
Approx. 160amp (1.6 times its current rating)
AS/NZS 3000 Clause 2.5.3.1(b)

## Slide 13
Continue
Question 12
The operating lever of a small air circuit breaker is in the ‘tripped’ position. What action is necessary to return the operating lever to the ON position (assuming that the fault has been cleared)?
Answer:
Switch it completely OFF then ON again.

## Slide 14
Continue
Question 13
What is the essential difference between the performance of a semi-enclosed rewireable fuse and an HRC fuse of the same current rating?
Answer:
An HRC fuse operates quicker and at a more predictable fault current value.

## Slide 15
Continue
Question 14
What value would you expect to read if the resistance of an 100 amp HRC fuse element was measured with a multimeter set on the OHMs x 1 range?
Answer:
Approximately zero ohms (less than 1 ohm)

## Slide 16
Continue
Question 15
List two possible reasons for an ‘undervoltage’ fault in a typical 3 phase electrical installation. What effect could it have on the operation of the installation?
Answer:
Possible reasons: Loss of a phase, overloading, fault conditions or high currents.
Possible effects: Lamp dimming and overcurrent in motors.

## Slide 17
Continue
Question 16
What does the abbreviation ACB stand for, when applied to an electrical component?
Answer:
Air Circuit Breaker

## Slide 18
Continue
Question 17
What is a typical ‘clearing time’ for an HRC fuse under extreme short circuit conditions?
Answer:
About 0.005 seconds (5ms)

## Slide 19
Continue
Question 18
What is the usual position of the operating lever in a typical moulded case circuit breaker, when it is in the ON position?
Answer:
Most circuit breakers are ON in the UP position.

## Slide 20
Continue
Question 19
What is the basic operational difference between a switch and a circuit breaker.
Answer:
A circuit breaker interrupts the circuit AUTOMATICALLY under short circuit conditions.

## Slide 21
Continue
Question 20
List three common types of fuse.
Answer:
HRC; rewireable; cartridge; thermal fuses.

## Slide 22
Continue
Question 21
What is the meaning of the term ‘inverse time’ when applied to circuit protection devices?
Answer:
As the fault current increases, the tripping time decreases. The higher the fault current, the faster the tripping time.

## Slide 23
Continue
Question 22
What effect causes the most damage when high, short duration fault currents occur in circuit conductors?
Answer:
High Magnetic Stresses

## Slide 24
Continue
Question 23
What is a typical ‘clearing time’ for a small moulded case air circuit breaker, under extreme short circuit conditions?
Answer:
About 0.002 seconds (2ms)

## Slide 25
Continue
Question 24
List four common measuring devices, which can be used to check an HRC fuse element for continuity.
Answer:
Multimeter; ohmmeter; Megger; battery test lamp; any continuity testing instrument.

## Slide 26
Continue
Question 25
What is the common name of each of the components, which make up what the Wiring Rules define as a ‘fuse’?
Answer:
The fuse BASE, the fuse WEDGE or CARRIER, the fusible ELEMENT (cartridge)

## Slide 27
Continue
Question 26
What effect does it have on the rupturing time of an HRC fuse as the fault current increases?
Answer:
Rupturing time decreases as the fault current increases.

## Slide 28
Continue
Question 27
Why is a semi-enclosed rewireable fuse not recommended as adequate protection in new installations?
Answer:
Because it is not reliable.

## Slide 29
Continue
Question 28
What is the main purpose of a circuit protection device?
Answer:
To protect a circuit from the potentially hazardous effects of overcurrent – such as heat and magnetic stress. Isolate the supply.

## Slide 30
Continue
Question 29
What is the main potentially hazardous effect of a short duration voltage spike or ‘spike’ in an installation?
Answer:
The high voltage may puncture the insulation in the circuit and cause a short circuit.

## Slide 31
Continue
Question 30
What is a Voltage Dependant Resistor (VDR)?
Answer:
A VDR is a special type of resistor, which decreases in resistance as the applied voltage increases.

## Slide 32
Continue
Question 31
What type of protection does a VDR provide?
Answer:
A VDR provides overvoltage protection for short duration voltage surges.

## Slide 33
Continue
Question 32
How is ‘no-volt’ protection usually provided in an electric motor circuit?
Answer:
By using a magnetic contactor to control the motor. If the voltage drops below a designed limit, the contactor coil de-energises and disconnects the contactor.

## Slide 34
Continue
Question 33
A particular fuse has a Category of Duty rating of A1. What is the maximum current the fuse is permitted to interrupt?
Answer:
1 kA or 1000 amps.

## Slide 35
Continue
Question 34
What additional type of protection must be provided in d.c. Circuits in which large electromagnetic coils, with many turns, are to be switched on and off?
Answer:
Protection against high induced voltages – usually a voltage dependant resistor connected in parallel to the coil.

## Slide 36
Continue
Question 35
List five types of circuit protection which apply to the selection and installation of control gear according to AS/NZS 3000?
Answer:
Short-circuit current; overcurrent; earth leakage current; overvoltage (surge protectors) & undervoltage. Clauses 2.5 to 2.8