## Slide 1: G063A Work Sheet 1
Click the left mouse button for each slide
(Or press the SPACEBAR or ENTER key)
S. G. Brooks. 2008
Risks.pps Version 6
Unit Title: G063A – Select and Arrange Equipment for General Electrical Installations
The purpose of this presentation is to provide you with the opportunity to answer the 26 questions from Work Sheet 1 of G063A .
Risks Associated with Electric Current Flow

## Slide 2: Question 1
Continue
What are the two main undesirable effects of high current passing through the human body?
Answer:
Electrocution and burns.

## Slide 3: Question 2
Continue
How can the risk of injury from unexpected mechanical movement, of electrically actuated equipment, be reduced?
Give the AS/NZS 3000:2018 clause number.
Answer:
Provide devices to disconnect or isolate equipment (e.g. interlocks).
AS/NZS 3000:2018 Clause 1.5.13.

## Slide 4: Question 3
Continue
What are the general requirements where insulation is the method for protecting against direct contact with live parts?
Give the AS/NZS 3000:2018 clause number.
Answer:
Live parts must be completely covered.
AS/NZS 3000:2018 Clause 1.5.4.3.

## Slide 5: Question 4
Continue
What degree of protection (IP rating) is needed where barriers provide the method for protecting against direct contact with live parts?
Give the AS/NZS 3000:2018 clause number.
Answer:
IPXXB. IP2X. IP4X
AS/NZS 3000:2018 Clause 1.5.4.4

## Slide 6: Question 5
Continue
What are the constructional requirements where barriers provide the method for protecting against direct contact with live parts?
Give the AS/NZS 3000:2018 clause number.
Answer:
Secured in place. Adequate strength. Restrictions on removal.
AS/NZS 3000:2018 Clause 1.5.4.4 (b)

## Slide 7: Question 6
Continue
What are the requirements where the method for protecting against direct contact with live parts is the provision of obstacles?
Give the AS/NZS 3000:2018 clause number.
Answer:
Access must be restricted to competent persons. Must prevent unintentional bodily contact.
AS/NZS 3000:2018 Clause 1.5.4.5.

## Slide 8: Question 7
Continue
What are the requirements where placing out of reach provides the method for protecting against direct contact with live parts?
Give the AS/NZS 3000:2018 clause number.
Answer: Access must be restricted to competent persons. Simultaneously accessible parts must not be within arms reach. AS/NZS 3000 Clause 1.5.4.6.

## Slide 9: Question 8
Continue
What is the intention of measures for protecting against indirect contact with live parts?
Give the AS/NZS 3000:2018 clause number.
Answer:
To protect against contact under fault conditions.
AS/NZS 3000:2018 Clauses 1.5.5 and 1.4.78

## Slide 10: Question 9
Continue
What is the purpose of automatic disconnection of supply when protecting against indirect contact with live parts?
Give the AS/NZS 3000:2018 clause number.
Answer:
To limit the touch voltage.
AS/NZS 3000:2018 Clause 1.5.5.3 (a)

## Slide 11: Question 10
Continue
If a fault exists between a live part and an exposed conductive part, the protective device must automatically disconnect the supply where the touch voltage exceeds what limits?
Give the AS/NZS 3000:2018 clause number.
Answer:
50 V a.c. and 120 V d.c.
AS/NZS 3000:2018 Clause 1.5.5.3 (b).

## Slide 12: Question 11
Continue
For fault loop impedance, the product of what two values must not exceed the nominal AC rms voltage to earth?
Give the AS/NZS 3000:2018 clause number.
Answer:
The impedance of the fault loop (Zs) at the fault, and the fault current (Ia).
AS/NZS 3000:2018 Clause 5.7.4

## Slide 13: Question 12
Continue
For a 240 volt final subcircuit comprising socket outlets, hand-held Class I equipment or other portable equipment, what is the maximum disconnection time for automatic disconnection devices?
Give the AS/NZS 3000:2018 clause number.
Answer:
0.4 seconds (400 ms)
AS/NZS 3000:2018 Clauses 1.5.5.3(d)(i) and 5.7.2 (a)

## Slide 14: Question 13
Continue
For a 240 volt final subcircuit supplying fixed equipment or submain, what is the maximum disconnection time for automatic disconnection devices?
Give the AS/NZS 3000:2018 clause number.
Answer:
5 seconds.
AS/NZS 3000:2018 Clauses 1.5.5.3(d)(i) and 5.7.2 (b)

## Slide 15: Question 14
Continue
It is possible to reduce the fault-loop impedance by bonding extraneous conductive parts to the protective earthing system.
What is the name given to this?
Give the AS/NZS 3000:2018 clause number.
Answer:
Yes. Equipotential bonding.
AS/NZS 3000:2018 Clauses 1.5.5.3 (e) and 5.6

## Slide 16: Question 15
Continue
What means are suitable for providing protection against dangerous voltages occurring on accessible conductive parts of electrical equipment in the event of a fault in the basic insulation?
Give the AS/NZS 3000:2018 clause number.
Answer:
Double insulation.
AS/NZS 3000:2018 Clause 1.5.5.4 (a)

## Slide 17: Question 16
Continue
What measures are not considered to provide a suitable insulation covering?
Give the AS/NZS 3000:2018 clause number.
Answer:
Paint. Varnish. Enamel.
AS/NZS 3000:2018 Clauses 1.5.4.3 (Note) and 1.5.5.4 (a) (Note1)

## Slide 18: Question 17
Continue
Briefly outline the measures for providing electrical separation.
Give the AS/NZS 3000:2018 clause number.
Answer:
Live parts not connected to any other circuit or earth. Isolating transformer. Double insulation between input and output.
AS/NZS 3000:2018 Clauses 1.5.5.5 and 7.4 to 7.4.3

## Slide 19: Question 18
Continue
What means are suitable for providing protection from the risk of ignition of flammable materials in normal service?
Give the AS/NZS 3000:2018 clause number.
Answer:
Proper design and installation so as to prevent adverse effect on electrical equipment. Screening and enclosures.
AS/NZS 3000:2018 Clauses 1.5.8 and 4.2.2.3

## Slide 20: Question 19
Continue
What means are suitable for providing protection from the risk of burns in normal service?
Give the AS/NZS 3000:2018 clause number.
Answer:
Proper design and installation so as to prevent adverse effect on electrical equipment.
Inaccessible and guards.
AS/NZS 3000:2018 Clauses 1.5.8 and 4.2.3

## Slide 21: Question 20
Continue
What means are suitable for protecting an installation from the effect of unwanted voltages?
Give the AS/NZS 3000:2018 clause number.
Answer:
Segregation. Terminate and protect conductors at both ends. Overvoltage protection.
AS/NZS 3000:2018 Clauses 1.5.11 See also Appendix F

## Slide 22: Question 21
Continue
What means are suitable for protecting an installation from the effect of over-current?
Give the AS/NZS 3000:2018 clause number.
Answer:
Automatic disconnection. Limiting overcurrent
AS/NZS 3000:2018 Clauses 1.5.9 and 2.5.1

## Slide 23: Question 22
Continue
What means are suitable for protecting an installation from the effect of Earth fault currents?
Give the AS/NZS 3000:2018 clause number.
Answer:
Conductors capable of carrying fault current without reaching excessive temperatures.
AS/NZS 3000:2018 Clauses 1.5.10 and 2.5.1

## Slide 24: Question 23
Continue
What means are suitable for protecting an installation from the effect of over voltage?
Give the AS/NZS 3000:2018 clause number.
Answer:
Segregation. Protection devices.
AS/NZS 3000:2018 Clauses 1.5.11.2 (a) & (b) and Appendix F

## Slide 25: Question 24
Continue
Under what conditions may a person come in ‘indirect contact’ with a live part.
Give the AS/NZS 3000:2018 clause number.
Answer:
When exposed conductive parts, of an electrical installation, become live under fault conditions due to damaged or faulty insulation.
AS/NZS 3000:2018 Clauses 1.5.5.1 and Appendix F

## Slide 26: Question 25
Continue
What is an electrical ‘interlock’?
Give the AS/NZS 3000:2018 clause number.
Answer:
A device intended to prevent mechanical movement of a part unless specified conditions are present (e.g. guards are in place) AS/NZS 3000:2018 Clauses 1.5.4.4 (b) (ii) and 1.5.13

## Slide 27: Question 26
Continue
What are three methods of providing protection against indirect contact with live parts in a 240 volt installation?
Give the AS/NZS 3000:2018 clause number.
Answer:
Automatic disconnection, double insulation, separation and limiting fault current.
AS/NZS 3000:2018 Clause 1.5.5.2

## Slide 28: The End
Click the left mouse button to exit
(Or press the SPACEBAR or ENTER key)
Thank you for participating in this presentation