## Slide 1
G063A Work Sheet 2
The purpose of this presentation is to provide you with the opportunity to answer the 49 questions from Work Sheet 2 of G063A .
Click the left mouse button for each slide
(Or press the SPACEBAR or ENTER key)
Version 2 G Fielding. 2020
Protective Earthing Systems.pps
Unit Title: G063A – Select and Arrange Equipment for General Electrical Installations
Protective Earthing Systems

## Slide 2: Question 1
Continue
What is the meaning of the term earthed? Give the AS/NZS3000:2018 clause number.
Answer:
Connected to both the supply neutral and the general mass of earth in accordance with the appropriate requirements of this standard.
Clause 1.4.47

## Slide 3
Continue
Question 2
What is the meaning of the term earthed situation? Give the AS/NZS3000:2018 clause number.
Answer:
A situation wherein there is a reasonable chance of a person touching exposed conductive parts and, at the same time, coming into contact with earth or any conductive medium that may be in electrical contact with the earth or through which a circuit may be completed to earth..
Clause 1.4.48

## Slide 4
Continue
Question 3
What is the meaning of the term equipotential bonding? Give the AS/NZS3000:2018 clause number.
Answer:
Electrical connections intended to bring exposed conductive parts to the same potential, but not intended to carry current in normal service.
Clause 1.4.60

## Slide 5
Continue
Question 4
What is the meaning of the term Multiple Earthed Neutral (MEN)? Give the AS/NZS3000:2018 clause number.
Answer:
Earthing in which the parts of an installation, required to be earthed are connected to the earth and the neutral conductor of the supply system.
Clause 1.4.83

## Slide 6
Continue
Question 5
What is the meaning of the term main earthing conductor? Give the AS/NZS3000:2018 clause number.
Answer:
A conductor connecting the main earthing terminal to the earth electrode
Clause 1.4.81

## Slide 7
Continue
Question 6
What is the meaning of the term protective earth? Give the AS/NZS3000:2018 clause number.
Answer:
A conductor connecting the earthing system to equipment required to be earthed.
Clause 1.4.100

## Slide 8
Continue
Question 7
What is the meaning of the term functional earthing? Give the AS/NZS3000:2018 clause number.
Answer:
An earth required to ensure correct operation of equipment
Clause 1.4.66 , 5.2.2

## Slide 9
Continue
Question 8
What is the main reason why single insulated 240v equipment must be earthed?
Answer:
To provide a mechanism for automatically disconnecting the supply in the case of an earth fault. To limit touch voltage.

## Slide 10
Continue
Question 9
What is the only permissible colour for an insulating earthing conductor? Give the AS/NZS3000:2018 clause or table number.
Answer:
Green/yellow
Table 3.4

## Slide 11
Continue
Question 10
Name the three recognised types of earthing systems referred to and indicate which one is covered within the Wiring Rules
Answer:
Multiple Earthed Neutral Direct Earthing ELCB (Voltage operated)
MEN - Clause 5.1.3

## Slide 12
Continue
Question 11
What is the maximum permissible resistance of a main earthing conductor or any equipotential bonding conductor?
Answer:
0.5Ω
Clause 8.3.5.2(b), 5.5.1.4

## Slide 13
Continue
Question 12
What is the minimum permissible size of a copper main earthing conductor Give the AS/NZS3000:2018 clause or table number.
Answer:
4 mm²
Clause 5.3.3.2 (PG279), Table 5.1 (PG278)

## Slide 14
Continue
Question 13
An Earthed Situation is where there is a reasonable chance of a person touching ………… and at the same time coming into contact with an earth. Give the AS/NZS clause number.
Answer:
Conductive parts
Clause 1.4.48

## Slide 15
Continue
Question 14
Any situation within ……… metres of a concrete floor or metal pipe is deemed to be an earthed situation. Give the AS/NZS clause or table number.
Answer:
2.5 meters
Clause 1.4.48 (a)

## Slide 16
Continue
Question 15
All parts of a …………… are deemed to be an earthed situation. Give the AS/NZS clause or table number.
Answer:
Bathroom, laundry, lavatory, toilet, or kitchen
Clause 1.4.48 (d)

## Slide 17
Continue
Question 16
Any situation which is external to a building and within ……… is deemed to be an earthed situation. Give the AS/NZS clause or table number.
Answer: External to a building
2.5 metres
Clause 1.4.48 (b)

## Slide 18
Continue
Question 17
Is it necessary to provide an earthing conductor to a lighting point consisting of a ceiling mounted batten holder installed inside a domestic building?
Answer:
Yes
Clause 5.4.3

## Slide 19
Continue
Question 18
Is it permissible to install a general purpose 10 amp socket-outlet without earthing the earthing contact?
Answer:
No
Clause 5.4.2

## Slide 20
Continue
Question 19
Is it necessary to earth accessible metal parts of a low or medium voltage equipment, if the accessible material is separated from live parts by double insulation?
Answer:
No
Clause 5.4.1.1(b)(i)

## Slide 21
Continue
Question 20
What type of earthing system is used in most installations in W.A.?
Answer:
MEN
Clause 5.1.3

## Slide 22
Continue
Question 21
Where is the protective earth connected to the neutral in a typical domestic installation?
Answer:
Switchboard – at the neutral link (usually at one end)
Clause 5.3.5.1 or figure 5.1

## Slide 23
Continue
Question 22
Is it necessary to earth metallic boxes which form part of a wiring system if they are isolated from all other conductive material (other than the metal which is earthed), and in no part accessible to personal contact?
Answer:
No
Clause 5.4.1.1(i)

## Slide 24
Continue
Question 23
Is it permissible to install bare MIMS cable without earthing the copper sheathing?
Answer:
No. Must be mechanically & electrically continuous
Clause 5.5.3.2 (b) & 5.5.4.3

## Slide 25
Continue
Question 24
An aluminium luminaire is to be installed outdoors on a wooden pole, three metres from the nearest earthed metal. Does the Wiring Rules require the exposed metal casing of the luminaire to be earthed?
Answer:
No
Clause 5.4.4 (Ex 3), 5.4.3 (2c)

## Slide 26
Continue
Question 25
Is it necessary to earth accessible metal parts of low voltage equipment if the accessible metal is to be separated from the live parts by double insulation?
Answer:
No
Clause 5.4.1.1 (b) (i)

## Slide 27
Continue
Question 26
What is the internationally recognised symbol which means Double Insulated - Do Not Earth?
Answer:
One Square inside another

## Slide 28
Continue
Question 27
What precaution must be taken to prevent an internal conductor from coming into contact with accessible metal if it becomes detached from its terminal in a double insulated appliance?
Answer:
It must be protected, secured or insulated so that it (or its single insulation) cannot come into contact with accessible metal.
Clause 5.4.1.1 (b) (Ex c)

## Slide 29
Continue
Question 28
Is it necessary to earth exposed metal in a 32 volt portable hand-lamp?
Answer:
No – Exposed conductive parts need not be earthed if supplied by a SELV or PELV system
Clause 5.4.1.1

## Slide 30
Continue
Question 29
Is it permissible to loop a MAIN earthing conductor into a luminaire to avoid having to run another earthing conductor to the luminaire?
Answer:
No
Clause 5.5.1.1

## Slide 31
Continue
Question 30
Is it permissible to connect a subsidiary earthing conductor to main earthing conductor using a soldered tee joint?
Answer:
Yes
Clause 5.5.2.1 (b)

## Slide 32
Continue
Question 31
Is it permissible to earth equipment by connecting exposed metal to an earthing conductor which is being used to earth equipment supplied from another distribution board?
Answer:
No
Clause 5.5.2.2.2

## Slide 33
Continue
Question 32
A steel wire armoured (SWA) cable is installed in such a way that the armouring is required to be earthed. At which point in the installation must the armouring be earthed?
Answer:
It must be earthed at the end adjacent to the switchboard or at the end where the cable originates
Clause 5.5.3.2 (b)

## Slide 34
Continue
Question 33
What limitation is placed on the use of metal conduit as the protective earthing conductor for cables which are contained in the conduit?
Answer:
The metallic enclosure and associated fittings must be electrically and mechanically continuous
Clause 5.5.4.2

## Slide 35
Continue
Question 34
A metal conduit is installed in such a way that it is required to be earthed. At which point in the installation must it be earthed?
Answer:
It must be earthed at the end adjacent to the switchboard or accessory in which the conduit originates
Clause 5.5.3.2 (a)

## Slide 36
Continue
Question 35
How must the hinged door of a metallic electrical cabinet be earthed?
Answer:
By connecting a flexible conductor between the fixed component of the cubical and the door.
Clause 5.3.2.3 (c) (ii) (b)

## Slide 37
Continue
Question 36
The exposed metal of electrical equipment on a wheeled overhead gantry crane is required to be earthed. Can metal to metal contact between the wheels and the rail be regarded as effective connection for the purposes of earthing ?
Answer:
Yes
Clause 5.3.2.3 (c) (iii) (B)

## Slide 38
Continue
Question 37
A particular electric motor is to be fixed in position using four bolts with nuts. Is it permissible to use one of the fixing bolts as the earth terminal?
Answer:
No
Clause 5.5.6.2 (b) (i) + (d)

## Slide 39
Continue
Question 38
What is the minimum permissible size of copper MAIN earthing conductor if the active conductor in the associated consumer’s mains is 16 square mm?
Answer:
6 square mm
Clause Table 5.1

## Slide 40
Continue
Question 39
What is the minimum permissible size of single core TPI cable (building wire) which can be used as an earthing conductor?
Answer:
2.5 square mm
Clause Table 5.1

## Slide 41
Continue
Question 40
In general, how must clamped joints be made in copper earthing conductors up to 4 square mm?
Answer:
Secured to prevent spreading
Clause 3.7.2.5

## Slide 42
Continue
Question 41
What is the minimum permissible diameter of a copper coated mild steel driven earthing electrode?
Answer:
12mm
Clause Table 5.2

## Slide 43
Continue
Question 42
Is it permissible to use rigid metallic conduit as a driven earth electrode?
Answer:
No
Clause Table 5.2

## Slide 44
Continue
Question 43
In general, where must a driven earth electrode be located ?
Answer:
Exposed to the weather, outside a building, separated from metallic enclosures of other buried surfaces
Clause 5.3.6.4 (a)

## Slide 45
Continue
Question 44
To what minimum depth must a driven earth electrode be driven?
Answer:
1.2 m
Clause 5.3.6.3 (a)

## Slide 46
Continue
Question 45
What action must be taken if exposed metal of a wiring enclosure is in unavoidable contact with metallic piping or other systems such as fire sprinklers, gas, or hot water?
Answer:
The metallic parts must be connected using an equipotential bonding conductor
Clause 5.6.2.3

## Slide 47
Continue
Question 46
What is the purpose of an equipotential bond in an installation?
Answer:
To minimise the risk associated with voltage differences between accessible metal parts
Clause 5.6.1, 1.4.52

## Slide 48
Continue
Question 47
What are two requirements for an effective earth joint?
Answer:
Joints must be electrically and mechanically sound
Clause 3.7.1

## Slide 49
Continue
Question 48
Is it necessary to earth the metal frame of a domestic installation?
Answer:
Yes
Clause 5.4.6.2

## Slide 50
Continue
Question 49
What are two general types of earthing conductor which need not be insulated?
Answer:
Aerials, braided conductors, busbars, MIMS sheaths, catenarys
Clause 5.3.2.4